## General Info
General Information Sheet |  |  | NO TOUCHY, TOUCHY IF TEXT IS BLACK
Job: | 56x60 Office | Job Name
Job #: | 24289
Date: | 2024-11-05
By:
Chk'd By:
Load Solar Time: | 5:00pm
Zone: | N/A
total building square footage | 3600 | this is used for Roof and Floor Only
Outside Dsgn Temp Heating (F): | 25 | based on location, If Triple code use -10
Outside Dsgn Temp Cooling (F): | 84 | based on location, If Triple code use 110
Inside Dsgn Temp Heating (F): | 72 | Per C302.1 IECC (Energy Code)
Inside Dsgn Temp Cooling (F): | 75 | Per C302.1 IECC (Energy Code)
Standard
Roof U value | 0.02 | 1 divided by r-value |  | Typically: | R-51 | R-30+R-20 (non Vented Roof)
Wall U value (Side Walls Only) | 0.038462 | 1 divided by r-value |  |  | R-21 | R-21+R3.2CI (Idaho sidewalls Only)
Wall U value (End Walls Only) | 0.038462 | 1 divided by r-value |  |  | R-21 | R-21+R5 (Triple Code per WA / 2021 IECC, ALL Walls)
Floor U value | 0.033333 | 1 divided by r-value |  |  | R-30
Glass U value | 0.28 | Min U-Value Per 2021 IECC
Glass SC | 0.68 | Double Glass with Thermal Break and 1/4" Air Space
Door U value | 0.083333 | Typical (1 divided by r-value)
Roll Up Door | 0.12987 | Typical (1 divided by r-value)
Store Front Door Value | 0.29412
People Sensible | 250
People Latent | 200 | Occupant at moderately active office work
Lights per SF | 1
Computers | 250
# of Exhaust Fans | 2
# of Doors @ 20sq ft (36x80) | 2 | Quantity of doors
# of Doors @ 21sq ft (36x84) | 0
# of Doors @ 32 sq ft (48x96) | 0
other doors (28sf) | 0
Group B - Office Facilities
Office sq ft | 0 | Total area Square Footage.
Lobby Area sq ft | 0
Conference Room sq ft | 0 |  | Printer | 130
Break area/kitchen sq ft | 0
Telephone / Data Room sq ft | 0
Printer Room | 0
Wall SQ FT |  | Wood | Container | Windows | Store Front
North | 0 | length x 10 | length x8 | 0 | 0
East | 0 | length x 9.5 | length x8 | 0 | 0
South | 0 | length x 10 | length x8 | 0 | 0
West | 0 | length x 9.5 | length x8 | 0 | 0
0
Education Group E
Art Room | 0 | Total area Square Footage.
Auditoriums | 0
Science Room | 0
Music Room | 0
Daycare 0-4 | 0
Classroom 5-8 | 0
Classroom 9+ | 0
Locker Room | 0
Medical
Office Area | 0 | Total area Square Footage.
Exam Room | 0
Wating Room | 0
Proceedure | 0
Residential
Bedroom | 0
Living Room | 0
Multipurpose Assembly
Kitchen
Note on B24: ibrown: Go to ASHRAE Data Sheet for Window Types
Note on B28: ibrown: Go to ASHRAE Data Sheet for People Loads
Note on B29: ibrown: Go to ASHRAE Data Sheet for People Loads

## ASHRAE data
Design Criteria that this sheet is currently set for is in blue.
44 Degree N. Latitude
| Jan. | Feb. | Mar. | Apr. | May. | June | July | Aug. | Sep. | Oct. | Nov. | Dec.
North | 17 | 22 | 27 | 33 | 36 | 47 | 37 | 34 | 28 | 23 | 18 | 15
NE | 17 | 43 | 87 | 136 | 162 | 169 | 159 | 132 | 80 | 42 | 18 | 15
East | 138 | 178 | 211 | 221 | 219 | 215 | 215 | 214 | 198 | 171 | 135 | 115
SE | 232 | 246 | 238 | 210 | 183 | 171 | 179 | 202 | 227 | 237 | 227 | 217
South | 252 | 247 | 218 | 171 | 132 | 115 | 128 | 165 | 211 | 239 | 248 | 246
SW | 232 | 246 | 238 | 210 | 183 | 171 | 179 | 202 | 227 | 237 | 227 | 217
W | 138 | 178 | 211 | 221 | 219 | 215 | 215 | 214 | 198 | 171 | 135 | 115
NW | 17 | 43 | 87 | 136 | 162 | 169 | 159 | 132 | 80 | 42 | 18 | 15
Horiz. | 109 | 160 | 206 | 240 | 257 | 261 | 254 | 236 | 199 | 157 | 109 | 89
SOLER TIME (CLF) FOR GLASS
WALL TYPE
LIGHT | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:30
North | 0.82 | 0.785 | 0.75 | 0.75 | 0.75 | 0.795 | 0.84 | 0.725 | 0.61
NE | 0.28 | 0.27 | 0.26 | 0.245 | 0.23 | 0.21 | 0.19 | 0.17 | 0.15
East | 0.29 | 0.27 | 0.25 | 0.235 | 0.22 | 0.205 | 0.19 | 0.17 | 0.15
SE | 0.37 | 0.35 | 0.33 | 0.305 | 0.28 | 0.26 | 0.24 | 0.215 | 0.19
South | 0.59 | 0.545 | 0.5 | 0.465 | 0.43 | 0.395 | 0.36 | 0.32 | 0.28
SW | 0.6 | 0.63 | 0.66 | 0.66 | 0.66 | 0.62 | 0.58 | 0.505 | 0.43
W | 0.45 | 0.51 | 0.57 | 0.605 | 0.64 | 0.625 | 0.61 | 0.525 | 0.44
NW | 0.33 | 0.4 | 0.47 | 0.53 | 0.59 | 0.595 | 0.6 | 0.51 | 0.42
Horiz. | 0.73 | 0.66 | 0.59 | 0.59 | 0.59 | 0.53 | 0.47 | 0.42 | 0.37
WALL TYPE
MEDIUM | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:30
North | 0.76 | 0.75 | 0.74 | 0.745 | 0.75 | 0.77 | 0.79 | 0.7 | 0.61
NE | 0.28 | 0.27 | 0.26 | 0.245 | 0.23 | 0.22 | 0.21 | 0.19 | 0.17
East | 0.29 | 0.275 | 0.26 | 0.245 | 0.23 | 0.22 | 0.21 | 0.19 | 0.17
SE | 0.36 | 0.345 | 0.33 | 0.31 | 0.29 | 0.27 | 0.25 | 0.23 | 0.21
South | 0.53 | 0.5 | 0.47 | 0.44 | 0.41 | 0.385 | 0.36 | 0.325 | 0.29
SW | 0.53 | 0.555 | 0.58 | 0.585 | 0.59 | 0.56 | 0.53 | 0.47 | 0.41
W | 0.4 | 0.45 | 0.5 | 0.53 | 0.56 | 0.555 | 0.55 | 0.48 | 0.41
NW | 0.3 | 0.36 | 0.42 | 0.465 | 0.51 | 0.525 | 0.54 | 0.465 | 0.39
Horiz. | 0.66 | 0.61 | 0.56 | 0.56 | 0.56 | 0.515 | 0.47 | 0.425 | 0.38
WALL TYPE
HEAVY | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:30
North | 0.72 | 0.71 | 0.7 | 0.7 | 0.7 | 0.725 | 0.75 | 0.66 | 0.57
NE | 0.26 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.2 | 0.185 | 0.17
East | 0.26 | 0.245 | 0.23 | 0.225 | 0.22 | 0.205 | 0.19 | 0.18 | 0.17
SE | 0.33 | 0.315 | 0.3 | 0.285 | 0.27 | 0.255 | 0.24 | 0.22 | 0.2
South | 0.5 | 0.465 | 0.43 | 0.4 | 0.37 | 0.345 | 0.32 | 0.29 | 0.26
SW | 0.52 | 0.54 | 0.56 | 0.56 | 0.56 | 0.525 | 0.49 | 0.43 | 0.37
W | 0.4 | 0.445 | 0.49 | 0.515 | 0.54 | 0.53 | 0.52 | 0.45 | 0.38
NW | 0.3 | 0.355 | 0.41 | 0.455 | 0.5 | 0.505 | 0.51 | 0.435 | 0.36
Horiz. | 0.62 | 0.565 | 0.51 | 0.51 | 0.51 | 0.465 | 0.42 | 0.385 | 0.35
| Jan.: Aluminum frame no thermal break (Uf=1.9); Mar.: Aluminum frame thermal break (Uf=1.0); May.: Wood or Vinyl Frame (Uf=0.4); Nov.: Degree of Activity | Typical Application | Total Heat Adults, Male, BTU/H | Total Heat, Adjusted, BTH/H | Sensible Heat, BTH/H | Latent Heat, BTU/H
| Jan.: R Value; Mar.: R Value; May.: R Value; Nov.: Seated at Theater | Theater - Matinee | 390 | 330 | 225 | 105
Single Glazing | Nov.: Seated at Theater | Theater - Evening | 390 | 350 | 245 | 105
Glass | Jan.: 1.31; Mar.: 1.09; May.: 0.9; Nov.: Seated, very light work | Offices, Hotels, Apartments | 450 | 400 | 245 | 155
1/8" Acrylic | Jan.: 1.26; Mar.: 1.02; May.: 0.84; Nov.: Moderately Active Office | Offices, Hotels, Apartments | 475 | 450 | 250 | 200
| Nov.: Standing, Light Work, Walking | Department Store, Retai Store | 550 | 450 | 250 | 200
Double Glass | Nov.: Walking, Standing | Drug Store, Bank | 550 | 500 | 250 | 250
1/4" Air Space | Jan.: 0.92; Mar.: 0.7; May.: 0.54; Nov.: Sedentary Work | Restaurant | 490 | 550 | 275 | 275
3/8" Air Space | Jan.: 0.88; Mar.: 0.66; May.: 0.5; Nov.: Light Bench Work | Factory | 800 | 750 | 275 | 475
1/2" and Greater Air Space | Jan.: 0.87; Mar.: 0.64; May.: 0.49; Nov.: Moderate Dancing | Dance Hall | 900 | 850 | 305 | 545
| Nov.: Walking, 3 mph; Light Machine Work | Factory | 1000 | 1000 | 375 | 625
Double Glass, e=0.40 | Nov.: Bowling | Bowling Alley | 1500 | 1450 | 580 | 870
1/4" Air Space | Jan.: 0.87; Mar.: 0.65; May.: 0.49; Nov.: Heavy Work | Factory | 1500 | 1450 | 580 | 870
3/8" Air Space | Jan.: 0.83; Mar.: 0.6; May.: 0.45; Nov.: Heavy Machine Work, Lifting | Factory | 1600 | 1600 | 635 | 965
1/2" and Greater Air Space | Jan.: 0.81; Mar.: 0.58; May.: 0.43; Nov.: Athletics | Gymnasium | 2000 | 1800 | 710 | 1090
Taken from ASHRAE Fundamentals Handbook 1989
Double Glass, e=0.15
1/4" Air Space | Jan.: 0.84; Mar.: 0.61; May.: 0.46
3/8" Air Space | Jan.: 0.78; Mar.: 0.56; May.: 0.41
1/2" and Greater Air Space | Jan.: 0.76; Mar.: 0.54; May.: 0.39
Double Glass
1/4" Argon Space | Jan.: 0.88; Mar.: 0.66; May.: 0.5
3/8" Argon Space | Jan.: 0.86; Mar.: 0.63; May.: 0.48
1/2" and Greater Argon Space | Jan.: 0.82; Mar.: 0.62; May.: 0.47
Double Glass, e=0.40
1/4" Argon Space | Jan.: 0.83; Mar.: 0.6; May.: 0.45
3/8" Argon Space | Jan.: 0.79; Mar.: 0.57; May.: 0.42
1/2" and Greater Argon Space | Jan.: 0.78; Mar.: 0.56; May.: 0.41
Double Glass, e=0.15
1/4" Argon Space | Jan.: 0.78; Mar.: 0.56; May.: 0.41
3/8" Argon Space | Jan.: 0.74; Mar.: 0.51; May.: 0.37
1/2" and Greater Argon Space | Jan.: 0.73; Mar.: 0.5; May.: 0.36
Double Glazing, 1/8" Acrylic or Polycarbonate
1/4" Air Space | Jan.: 0.89; Mar.: 0.67; May.: 0.51
3/8" Air Space | Jan.: 0.86; Mar.: 0.64; May.: 0.48
1/2" and Greater Air Space | Jan.: 0.85; Mar.: 0.62; May.: 0.47
Double Glazing, 1/4" Acrylic or Polycarbonate
1/4" Air Space | Jan.: 0.86; Mar.: 0.64; May.: 0.48
3/8" Air Space | Jan.: 0.84; Mar.: 0.61; May.: 0.46
1/2" and Greater Air Space | Jan.: 0.82; Mar.: 0.6; May.: 0.45
Triple Glass
1/4" Air Space | Jan.: 0.79; Mar.: 0.57; May.: 0.42
3/8" Air Space | Jan.: 0.76; Mar.: 0.54; May.: 0.39
1/2" and Greater Air Space | Jan.: 0.75; Mar.: 0.53; May.: 0.38
Triple Glass, e=0.40
1/4" Air Space | Jan.: 0.77; Mar.: 0.55; May.: 0.4
3/8" Air Space | Jan.: 0.74; Mar.: 0.52; May.: 0.37
1/2" and Greater Air Space | Jan.: 0.72; Mar.: 0.5; May.: 0.36
Triple Glass or Double Glass with Polyester Film Suspended in Between, e=0.15 on Surface 2, 3, 4, or 5
1/4" Air Space | Jan.: 0.76; Mar.: 0.53; May.: 0.39
3/8" Air Space | Jan.: 0.72; Mar.: 0.5; May.: 0.35
1/2" and Greater Air Space | Jan.: 0.7; Mar.: 0.48; May.: 0.34
Triple Glass or Double Glass with Polyester Film Suspended in Between, e=0.15 on Surfaces 2 or 3, and 4 or 5
1/4" Air Space | Jan.: 0.73; Mar.: 0.53; May.: 0.36
3/8" Air Space | Jan.: 0.69; Mar.: 0.47; May.: 0.32
1/2" and Greater Air Space | Jan.: 0.67; Mar.: 0.45; May.: 0.31
Triple Glass
1/4" Argon Space | Jan.: 0.77; Mar.: 0.54; May.: 0.39
3/8" Argon Space | Jan.: 0.74; Mar.: 0.52; May.: 0.37
1/2" and Greater Argon Space | Jan.: 0.73; Mar.: 0.51; May.: 0.36
Triple Glass, e=0.40
1/4" Argon Space | Jan.: 0.74; Mar.: 0.52; May.: 0.37
3/8" Argon Space | Jan.: 0.72; Mar.: 0.49; May.: 0.35
1/2" and Greater Argon Space | Jan.: 0.71; Mar.: 0.48; May.: 0.34
Triple Glass or Double Glass with Polyester Film Suspended in Between, e=0.15 on Surface 2, 3, 4, or 5
1/4" Argon Space | Jan.: 0.72; Mar.: 0.5; May.: 0.35
3/8" Argon Space | Jan.: 0.69; Mar.: 0.47; May.: 0.33
1/2" and Greater Argon Space | Jan.: 0.68; Mar.: 0.46; May.: 0.31
Triple Glass or Double Glass with Polyester Film Suspended in Between, e=0.15 on Surfaces 2 or 3, and 4 or 5
1/4" Argon Space | Jan.: 0.69; Mar.: 0.47; May.: 0.32
3/8" Argon Space | Jan.: 0.66; Mar.: 0.44; May.: 0.3
1/2" and Greater Argon Space | Jan.: 0.65; Mar.: 0.43; May.: 0.29
Taken from ASHRAE Fundamentals Handbook 1989

## Clg Block - Block
Cooling Load Calc. Sheet
| Job: | 56x60 Office |  | Time: |  | 5:00pm
| Job #: | 24289 |  | Zone: |  | Block
| Date: | 2024-11-05 |  | Area or Room Name: |  | Block
| By: | 0 |  | Outside Dsgn Temp (F): |  | 84
| Chk'd By: | 0 |  | Inside Dsgn Temp (F): |  | 75
|  |  |  | Floor Area (sq. ft.): |  | 3600
Roof |  | Area | U-value | DT |  |  |  | Sensible | Latent
|  | 3600 | 0.02 | 34 |  |  |  | 2448
[7 empty] | Subtotal: | 2448
Wall |  | Area | U-value | DT |  |  |  | Sensible | Latent
| North | 0 | 0.038462 | 9 |  |  |  | 0
| East | 0 | 0.038462 | 14 |  |  |  | 0
| South | 0 | 0.038462 | 14 |  |  |  | 0
| West | 0 | 0.038462 | 14 |  |  |  | 0
[7 empty] | Subtotal: | 0
Floor |  | Area | U-value | DT |  |  |  | Sensible | Latent
|  | 3600 | 0.033333 | 9 |  |  |  | 1080 | [5 empty] | sqft of each space
[7 empty] | Subtotal: | 1080
[10 empty] | Outdoor Ventillation Requirments per 2021 IMC section 403.3 (Office Area) | [6 empty] | Mixed Air Temp Calculation (TRA x (%TRA) + TOSA x (%TOSA)
Solar |  | Area | SHGF | CLF | SC |  |  | Sensible | Latent |  | Rp | Pz | Ra | Az | Occy/1000 s. ft | Total cfm | RA | 1200 | cfm
| North | 0 | 47 | 0.72 | 0.68 |  |  | 0 |  | Office Area | 5 | 0 | 0.06 | 0 | 5 | 0 | RAT | 70 | deg F.
| East | 0 | 215 | 0.29 | 0.68 |  |  | 0 |  | Lobbies | 5 | 0 | 0.06 | 0 | 10 | 0 | OAT | -14 | deg F.
| South | 0 | 115 | 0.55 | 0.68 |  |  | 0 |  | Confrence Rm | 5 | 0 | 0.06 | 0 | 50 | 0 | %RA | 0.7 | %
| W | 0 | 215 | 0.54 | 0.68 |  |  | 0 |  | Break Area | 7.5 | 0 | 0.18 | 0 | 70 | 0 | %OSA | 0.3 | %
| Horiz. | 0 | 261 | 0.64 | 0.68 |  |  | 0 |  | Tele/Data Room | 5 | 0 | 0.06 | 0 | 60 | 0
[7 empty] | Subtotal: | 0 |  | Printer Room | 5 | 0 | 0.06 | 0 | 4 | 0 | MAT= | 44.8 | deg.F
[10 empty] | Subtotal |  | 0 |  | 0 |  | 0
Glazing |  | Area | U-value | DT |  |  |  | Sensible | Latent | OSA= | 0 | 0 |  |  |  |  | BTU Requirements
|  | 0 | 0.28 | 9 |  |  |  | 0 | [8 empty] | SAT | 105 | deg F.
[7 empty] | Subtotal: | 0 |  | Pz=People per zone | [6 empty] | Delta "T" | 60.2 | deg F.
[10 empty] | Az=Zone floor area | [6 empty] | AS Constant | 1.05
Metal Door |  | Area | U-value | DT |  |  |  | Sensible | Latent | Rp=CFM/ person (table 403.3.1.1) | [6 empty] | Total BTU | 75852 | BTU/H
|  | 40 | 0.083333 | 9 |  |  |  | 30 |  | Ra=CFM/Ft (table 403.3.1.1) | [6 empty] | Total KW | 22.2309 | kW
|  | 0 | 0.12987 | 9 |  |  |  | 0 |  | Occupancy per 1000 sq. f.t (table 403.3.1.1)
[7 empty] | Subtotal: | 30
Outdoor Ventillation Requirments per 2021 IMC section 403.3 (Education)
Storefront Door |  | Area | U-value | DT |  |  |  | Sensible | Latent |  | Rp | Pz | Ra | Az | Occy/1000 s. ft | Total cfm
|  | 0 | 0.29412 | 9 |  |  |  | 0 |  | Art Classroom | 10 | 0 | 0.18 | 0 | 20 | 0
[7 empty] | Subtotal: | 0 |  | Auditoriums | 5 | 0 | 0.06 | 0 | 150 | 0
[10 empty] | Science | 10 | 0 | 0.18 | 0 | 25 | 0
People |  | # of | Sensible | Latent |  |  |  | Sensible | Latent | Music/Theater | 10 | 0 | 0.06 | 0 | 35 | 0
|  | Occupants | /person | /person | [5 empty] | Daycare 0-4 | 10 | 0 | 0.18 | 0 | 25 | 0
|  | 0 | 250 | 200 |  |  |  | 0 | 0 | Classroom 5-8 | 10 | 0 | 0.12 | 0 | 25 | 0
[7 empty] | Subtotal: | 0 | 0 | Classroom 9+ | 10 | 0 | 0.12 | 0 | 35 | 0
[10 empty] | Locker Room | 0.25 | 0 | N/A | 0 | N/A | 0
Lights |  | Area | Watts/Sq | Total |  |  |  | Sensible | Latent | Subtotal |  | 0 |  | 0 |  | 0
|  | 3600 | 1 | 3600 |  |  |  | 12286.8 |  | OSA= | 0
[7 empty] | Subtotal: | 12286.8
Pz=People per zone
Misc. Equip. |  | Items | Watts per | Total |  |  |  | Sensible | Latent | Az=Zone floor area
| Computers | 8 | 250 | 2000 |  |  |  | 6826 | 1706.5 | Rp=CFM/ person (table 403.3.1.1)
| Misc. | 0 | 800 | 0 |  |  |  | 0 | 0 | Ra=CFM/Ft (table 403.3.1.1)
|  | 0 |  | 0 |  |  |  | 0 | 0 | Occupancy per 1000 sq. f.t (table 403.3.1.1)
[7 empty] | Subtotal: | 6826 | 1706.5
OSA |  | Total | Grains/lb | Evap. | OSA db | Room |  | Sensible | Latent
|  | OSA |  | hfg |  | Temp |  |  |  | Outdoor Ventillation Requirments per 2021 IMC section 403.3 (Medical)
|  | 0 | 20 | 970 | 84 | 75 |  | 0 | 0 |  | Rp | Pz | Ra | Az | Occy/1000 s. ft | Total cfm
[7 empty] | Subtotal: | 0 | 0 | Office Area | 5 | 0 | 0.06 | 0 | 5 | 0
[10 empty] | Exam Room | 15 | 0 | N/A | 0 | 20 | 0
HRV/ERV 200s |  | 0 |  |  |  |  | Totals for Area: | 22670.8 | 1706.5 | Wating Room | 5 | 0 | 0.06 | 0 | 30 | 0
[7 empty] | Totals : | 24377.3 |  | Proceedure | 15 | 0 | N/A | 0 | 20 | 0
[7 empty] | Tons: | 2.0314 |  | Subtotal |  | 0 |  | 0 |  | 0
[10 empty] | OSA= | 0
Pz=People per zone
Az=Zone floor area
Rp=CFM/ person (table 403.3.1.1)
Ra=CFM/Ft (table 403.3.1.1)
Occupancy per 1000 sq. f.t (table 403.3.1.1)
Outdoor Ventillation Requirments per 2021 IMC section 403.3 (Residential)
[11 empty] | Rp | Pz | Ra | Az | Occy/1000 s. ft | Total cfm
[10 empty] | Bedroom | 5 | 0 | 0.06 | 0 | 10 | 0
[10 empty] | Living Room | 5 | 0 | 0.06 | 0 | 10 | 0
[10 empty] | Multipurpose Assembly | 5 | 0 | 0.06 | 0 | 120 | 0
[10 empty] | Kitchen | 15 | 0 | N/A | 0 | 20 | 0
[10 empty] | Subtotal |  | 0 |  | 0 |  | 0
[10 empty] | OSA= | 0
Pz=People per zone
Az=Zone floor area
Rp=CFM/ person (table 403.3.1.1)
Ra=CFM/Ft (table 403.3.1.1)
Occupancy per 1000 sq. f.t (table 403.3.1.1)
Note on F67: ibrown: temperature difference between supply and return

## Htg Block - Block
Heating Load Calc. Sheet
| Job: | 56x60 Office |  | Time: |  | 5:00pm
| Job #: | 24289 |  | Zone: |  | Block
| Date: | 2024-11-05 |  | Area or Room Name: |  | Block
| By: | 0 |  | Outside Dsgn Temp (F): |  | 25
| Chk'd By: | 0 |  | Inside Dsgn Temp (F): |  | 72
|  |  |  | Floor Area (sq. ft.): |  | 3600
Roof |  | Area | U-value | DT |  |  |  | Sensible
|  | 3600 | 0.02 | 47 |  |  |  | 3384
[7 empty] | Subtotal: | 3384
Floor |  | Area | U-value | DT |  |  |  | Sensible
|  | 3600 | 0.033333 | 40 |  |  |  | 4800
[7 empty] | Subtotal: | 4800
Wall |  | Area | U-value | DT |  |  |  | Sensible
| North | 0 | 0.038462 | 47 |  |  |  | 0
| East | 0 | 0.038462 | 47 |  |  |  | 0
| South | 0 | 0.038462 | 47 |  |  |  | 0
| West | 0 | 0.038462 | 47 |  |  |  | 0
[7 empty] | Subtotal: | 0
Metal Door |  | Area | U-value | DT |  |  |  | Sensible
|  | 40 | 0.083333 | 47 |  |  |  | 156.6667
|  | 0 | 0.12987 | 47 |  |  |  | 0
[7 empty] | Subtotal: | 156.6667
Storefront Door |  | Area | U-value | DT |  |  |  | Sensible
|  | 0 | 0 | 47 |  |  |  | 0
[7 empty] | Subtotal: | 0
Glazing |  | Area | U-value | DT |  |  |  | Sensible
|  | 0 | 0.28 | 47 |  |  |  | 0
[7 empty] | Subtotal: | 0
OSA |  | Ventillation | Exhaust | total | DT |  |  | Sensible
|  | OSA | OSA | OSA
|  | 0 | 200 | 200 | 47 |  |  | 9400
[7 empty] | Subtotal: | 9400
[7 empty] | Totals for Area: | 17740.6667
[7 empty] | kW | 5.1934