## Occupant Calculator
CBC Section 1004 / IBC Section 1004
Occupancy Use: | Occupant Load Factor: | Square Footage: | # Of Persons
Accesory Storage, Mechanical Equipment | 300 Gross | 0 | 0
Assembly (Casino) | 11 Gross | 0 | 0
Assembly (With Tables & Chairs) | 15 Net | 0 | 0 | <--- Use for Conference Rooms & Break Rooms
Assembly (Concentrated) | 7 Net | 0 | 0
Assembly (Standing) | 5 Net | 0 | 0
Business (2006 - 2015 IBC) | 100 Gross | 0 | 0
Business (2018 IBC & 2019 CBC) | 150 Gross | 50000 | 333.4
Courtrooms | 40 Net | 0 | 0
Day Care | 35 Net | 0 | 0
Dormatories | 50 Gross | 0 | 0
Educational (Includes Adult Education) | 20 Net | 0 | 0 | 0
Exercise Rooms | 50 Gross | 0 | 0
Institutional (Inpatient) | 240 Gross | 0 | 0
Institutional (Outpatient) | 100 Gross | 0 | 0
Institutional (Sleeping Areas) | 120 Gross | 0 | 0 |  | Note:
Commercial Kitchens | 200 Gross | 0 | 0 |  | Gross: overall area (including walls)
Lab (Educational) | 50 Net | 0 | 0 |  | Net: actual wall-to-wall square footage
Lab (Non-Educational) | 100 Net | 0 | 0
Library (Reading Rm) | 50 Net | 0 | 0
Library (Stack Areas) | 100 Gross | 0 | 0
Locker Rooms | 50 Gross | 0 | 0
Mercantile | 60 Gross | 0 | 0
Mercantile (Storage, Stock) | 300 Gross | 0 | 0
| TOTAL # OF OCCUPANTS: |  | 333.4

## IMC-UMC Vent. Rate
IMC MINIMUM VENTILATION RATE:
BUILDING USE: | PEOPLE OUTDOOR FLOW RATE (Rp): | AREA OUTDOOR FLOW RATE (Ra): | OCCUPANT DENSITY /1000 sq. ft.: | SQUARE FOOTAGE OF BDLG/AREA (Az): | TOTAL OUTDOOR AIR REQUIRED (Vbz=RpPz+RaAz): | EXHAUST REQUIRED: | OCCUPANT LOAD OF SPACE (Pz) | ZONE OUTDOOR AIRFLOW (Voz & Vot) COOLING | ZONE OUTDOOR AIRFLOW (Voz & Vot) HEATING
OFFICES
OFFICE SPACE(S) | 5 | 0.06 | 5 | 50000 | 4250 | - | 250 | 4250 | 5312.5
CONFERENCE ROOMS | 5 | 0.06 | 50 | 0 | 0 | - | 0 | 0 | 0
RECEPTION AREA | 5 | 0.06 | 30 | 0 | 0 | - | 0 | 0 | 0
COPY / PRINTING RM | 5 | 0.06 | 4 | 0 | 0 | 0 | 0 | 0 | 0
LOBBIES | 5 | 0.06 | 10 | 0 | 0 | - | 0 | 0 | 0
DINING ROOM | 7.5 | 0.18 | 70 | 0 | 0 | - | 0 | 0 | 0
CAFETERIA | 7.5 | 0.18 | 100 | 0 | 0 | - | 0 | 0 | 0
PHARMACY PREP AREA | 5 | 0.18 | 10 | 0 | 0 | - | 0 | 0 | 0
|  |  |  | TOTAL OUTDOOR AIR REQUIRED: | 4250
EDUCATIONAL
CLASSROOM (5-8) | 10 | 0.12 | 25 | 0 | 0 | - | 0 | 0 | 0
CLASSROOM (9+) | 10 | 0.12 | 35 | 0 | 0 | - | 0 | 0 | 0
DAYCARE (UP TO 4YR) | 10 | 0.18 | 25 | 0 | 0 | - | 0 | 0 | 0
AUDITORIUMS | 5 | 0.06 | 150 | 0 | 0 | - | 0 | 0 | 0
ART CLASSROOM | 10 | 0.18 | 20 | 0 | 0 | 0 | 0 | 0 | 0
SCIENCE LAB | 10 | 0.18 | 25 | 0 | 0 | 0 | 0 | 0 | 0
WOOD/METAL SHOP | 10 | 0.18 | 20 | 0 | 0 | 0 | 0 | 0 | 0
COMPUTER LAB | 10 | 0.12 | 25 | 0 | 0 | - | 0 | 0 | 0
MULTIUSE ASSEMBLY | 7.5 | 0.06 | 100 | 0 | 0 | - | 0 | 0 | 0
|  |  |  | TOTAL OUTDOOR AIR REQUIRED: | 0
PUBLIC SPACES / GENERAL USE
CORRIDORS | - | 0.06 | 0 | 0 | 0 | - | 0 | 0 | 0
RELIGIOUS WORSHIP | 5 | 0.06 | 120 | 0 | 0 | - | 0 | 0 | 0
COURTROOMS | 5 | 0.06 | 70 | 0 | 0 | - | 0 | 0 | 0
AEROBICS ROOM | 20 | 0.06 | 40 | 0 | 0 | - | 0 | 0 | 0
COPY / PRINTING ROOM | - | - | - | 0 | - | 0 | - | - | -
JANITOR CLOSET (UMC/CMC) | - | - | - | 0 | - | 0 | - | - | -
WEIGHT ROOM | 20 | 0.06 | 10 | 0 | 0 | - | 0 | 0 | 0
LOCKER (ATHLETIC / HEALTH CARE) | - | - | - | 0 | - | 0 | - | - | -
LOCKER/DRESSING RM (OTHER) | - | - | - | 0 | - | 0 | - | - | -
SOILED LAUNDRY STORAGE | - | - | - | 0 | - | 0 | - | - | -
SHOWER (PER HEAD) | TOTAL # OF SHOWERS: |  | 1 | - | - | 50 | - | - | -
TOILET ROOMS | TOTAL # OF W.C. / URINALS: |  | 2 | - | - | 140 | - | - | -
|  |  |  | TOTAL OUTDOOR AIR REQUIRED: | 0
RETAIL
SALES | 7.5 | 0.12 | 15 | 0 | 0 | - | 0 | 0 | 0
DRESSING ROOMS | - | - | - | 0 | - | 0 | - | - | -
STORAGE ROOMS | - | 0.12 | - | 0 | 0 | - | - | - | -
|  |  |  | TOTAL OUTDOOR AIR REQUIRED: | 0
|  |  |  | GRAND TOTAL OF OUTDOOR AIR REQUIRED: | 4250 |  | 1 | (D=Ps/Pz)
(Vou=D x Eall zone RpPz + Eall zones RaAz)
|  |  |  | TOTAL EXHAUST AIR: | 190
Note: HVAC sizing should be considered base on total exhaust from room/space.

## IMC-UMC Endmount HVAC Calc
WALL MOUNT HVAC'S | [5 empty] | BARD WALL MOUNT OUTDOOR AIR VENTILATION: | [6 empty] | 2009 IECC | SEER: | EER: |  | IECC Climate Zone: |  |  | 2012 IECC | SEER: | EER: | IECC Climate Zone: |  | 2015 IECC | SEER: | EER: | IECC Climate Zone: |  | 2018 IECC | SEER: | EER: | IECC Climate Zone: |  | 2019 CEC | SEER: | EER: | 1 | Doesn't Meet
A/C SIZE: | # OF A/C's: | VENTILATION TYPE: | VENTILATION RATE: | COOLING BTU: |  | HVAC SIZE: | SYSTEM CFM OUTPUT: | F.A.D. | C.R.V. | ECONOMIZER | HVAC HEAT STRIP BTHU CONV. |  | Bard AC | - | 9 | 1A | Not Required |  |  | Bard AC | - | 9 | 1A | Not Required | Bard AC | - | 9 | 1A | Not Required | Bard AC | - | 9 | 1A | Not Required | Bard AC | - | 11 | 2 | Doesn't Meet
3 TON | 4 | ECONOMIZER | 4600 | 36,000 |  | N/A | 0 | 0 | 0 | 0 | ENTER KW: | 0 | Bard HP | - | 9 | 1B | Not Required |  |  | Bard HP | - | 9 | 1B | Not Required | Bard HP | - | 9 | 1B | Not Required | Bard HP | - | 9 | 1B | Not Required | Bard HP | - | 11 | 3 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  | 1 TON | 420 | 105 | 210 | 420 | = BTHU: | 0 | Roof Top AC (1P) | 13 | 11.18 | 2A | Not Required |  |  | Roof Top AC (1P) | 13 | 11.18 | 2A | No Exception | Roof Top AC (1P) | 14 | 11.76 | 2A | No Exception | Roof Top AC (1P) | 14 | 11.76 | 2A | Meets Exception | Roof Top AC (1P) | 14 | 11 | 4 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  | 1.5 TON | 600 | 150 | 300 | 600 |  |  | Roof Top AC (3P) | 13 | 11.18 | 2B | Meets Exception |  |  | Roof Top AC (3P) | 13 | 11.18 | 2B | Meets Exception | Roof Top AC (3P) | 14 | 11.76 | 2B | Meets Exception | Roof Top AC (3P) | 14 | 11.76 | 2B | Meets Exception | Roof Top AC (3P) | 14 | 11 | 5 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  | 2 TON | 800 | 200 | 400 | 800 |  |  | Roof Top HP (1P) | 13 | 11.18 | 3A | No Exception |  |  | Roof Top HP (1P) | 13 | 11.18 | 3A | No Exception | Roof Top HP (1P) | 14 | 11.76 | 3A | No Exception | Roof Top HP (1P) | 14 | 11.76 | 3A | Meets Exception | Roof Top HP (1P) | 14 | 11 | 6 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  | 2.5 TON | 950 | 237.5 | 475 | 950 | IECC ECONOMIZER REQUIREMENTS: |  | Roof Top HP (3P) | 13 | 11.18 | 3B | Meets Exception |  |  | Roof Top HP (3P) | 13 | 11.18 | 3B | Meets Exception | Roof Top HP (3P) | 14 | 11.76 | 3B | Meets Exception | Roof Top HP (3P) | 14 | 11.76 | 3B | Meets Exception | Roof Top HP (3P) | 14 | 11 | 7 | Doesn't Meet
[6 empty] | 3 TON | 1150 | 287.5 | 575 | 1150 | 2009 | OVER 4.5 TON / > 300,00 BTU | Split System | 13 | 11.18 | 3C | No Exception |  |  | Split System | 13 | 11.18 | 3C | No Exception | Split System | 13 | 11.18 | 3C | No Exception | Split System | 13 | 11.18 | 3C | No Exception | Split System | 13 | 12.2 | 8 | Doesn't Meet
[6 empty] | 3.5 TON | 1350 | 337.5 | 675 | 1350 | 2012 | OVER 2.5 TON / > 300,000 BTU | Minisplit AC | 13 | 11.18 | 4A | No Exception |  |  | Minisplit AC | 13 | 11.18 | 4A | No Exception | Minisplit AC | 13 | 11.18 | 4A | No Exception | Minisplit AC | 13 | 11.18 | 4A | Meets Exception | Minisplit AC | 13 | 11.18 | 9 | Doesn't Meet
[6 empty] | 4 TON | 1550 | 387.5 | 775 | 1550 | 2015 | OVER 4.5 TON / > 300,00 BTU | Thru Wall | 12 | 10.56 | 4B | Meets Exception |  |  | Thru Wall | 12 | 10.56 | 4B | Meets Exception | Thru Wall | 12 | 10.56 | 4B | Meets Exception | Thru Wall | 12 | 10.56 | 4B | Meets Exception | Thru Wall | - | 9.3 | 10 | Doesn't Meet
[6 empty] | 5 TON | 1750 | 437.5 | 875 | 1750 | 2018 | OVER 4.5 TON / > 300,00 BTU | PTAC | - | -0.28 | 4C | No Exception |  |  | PTAC | - | -4.2 | 4C | No Exception | PTAC | - | -4 | 4C | No Exception | PTAC | - | -4 | 4C | No Exception | PTAC | - | 1.22 | 11 | Doesn't Meet
[16 empty] | 5A | No Exception | [5 empty] | 5A | No Exception |  |  |  | 5A | No Exception |  |  |  | 5A | No Exception |  |  |  | 12 | Doesn't Meet
OUTDOOR AIR PROPOSED: | TOTAL NEEDED: | ADD'L REQUIRED: | TOTAL COOLING BTU: | BTU REDUCTION BASED ON FRESH AIR TYPE: |  | VENTILATION REQUIREMENT: | [9 empty] | 5B | No Exception | [5 empty] | 5B | No Exception |  |  |  | 5B | No Exception |  |  |  | 5B | No Exception |  |  |  | 13 | Doesn't Meet
4600 | 4250 | NO ADD'L NEEDED | 144000 | 0 |  | NO ADD'L VENTILATION REQUIRED | [6 empty] | Not Required |  |  | 5C | No Exception |  |  | No Exception |  |  | 5C | No Exception | No Exception |  |  | 5C | No Exception | Meets Exception |  |  | 5C | No Exception | #REF! |  |  | 14 | Doesn't Meet
[6 empty] | Note: 2012 IECC: HVAC's 3-Ton or Greater require Economizers | [9 empty] | 6A | No Exception | [5 empty] | 6A | No Exception |  |  |  | 6A | No Exception |  |  |  | 6A | No Exception |  |  |  | 15 | Doesn't Meet
NOTES: | [15 empty] | 6B | No Exception | [5 empty] | 6B | No Exception |  |  |  | 6B | No Exception |  |  |  | 6B | No Exception |  |  |  | 16 | Doesn't Meet
1. WHEN ECONOMIZERS ARE REQUIRED OVER 300,000 BTU, LOOK AT CHART AND BRING THE TOTAL UNDER 300,000. NOT ALL HVAC'S NEED ECONOMIZERS. | [15 empty] | 7 | Not Required | [5 empty] | 7 | No Exception |  |  |  | 7 | Not in 2015 Code |  |  |  | 7 | Not in 2018 Code
2. WHEN CRV'S ARE REQUIRED, LOOK AT CHART AND MEET THE ADDITIONAL REQUIRED. NOT ALL HVAC'S NEED CRV'S IN CASES. | [15 empty] | 8 | Not Required | [5 empty] | 8 | No Exception |  |  |  | 8 | Not in 2015 Code |  |  |  | 8 | Not in 2018 Code
ECONOMIZER EXCEPTION
Code Year: | HVAC Size (Tons): | HVAC Type: | IECC Climate Zone: | Min. EER Rating: | Min. SEER Rating: | Equipment EER Rating: | Equipment SEER Rating: | Results: |  |  |  |  | PMI Elec. Equip. |  | Equipment Size EER Rating
2015 IECC | 5 | Bard AC | 2A | 9 | - | 11 | - | No Exception | [6 empty] | 0.75 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5
[14 empty] | Bard AC | - | 11 | 11.3 | 11.2 | 11.2 | 11 | 11 | 11 | 11
[14 empty] | Bard HP | - | - | 11 | 11 | 11 | 11 | 11 | 11 | 11
[14 empty] | Roof Top AC (1P) | - | - | - | - | - | 12.5 | 12.5 | 12 | 12
[14 empty] | Roof Top AC (3P) | - | - | - | - | - | 13 | 13 | 12.5 | 12.5
[14 empty] | Roof Top HP (1P) | - | - | - | - | - | 13 | 13 | 12 | 12
[14 empty] | Roof Top HP (3P) | - | - | - | - | - | 13 | 13 | 12.5 | 12.5
[14 empty] | Minisplit AC | 10.4 | 10.6 | 12.2 | 9.2 | - | - | - | - | -
Split System
Thru Wall
PTAC
[13 empty] | PMI Elec. Equip. |  | Equipment Size SEER Rating
[15 empty] | 0.75 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5
[14 empty] | Bard AC | - | - | - | - | - | - | - | - | -
[14 empty] | Bard HP | - | - | - | - | - | - | - | - | -
[14 empty] | Roof Top AC (1P) | - | - | - | - | - | 15 | 15 | 15 | 15
[14 empty] | Roof Top AC (3P) | - | - | - | - | - | 15 | 15 | 15 | 15
[14 empty] | Roof Top HP (1P) | - | - | - | - | - | 15.5 | 15.5 | 15 | 15
[14 empty] | Roof Top HP (3P) | - | - | - | - | - | 15 | 15 | 15 | 15
[14 empty] | Minisplit AC | 16 | 16 | 16 | 16 | - | - | - | - | -
Split System
Thru Wall
PTAC

## IMC-UMC Rooftop HVAC Calc
RTU HVAC'S | [6 empty] | DAIKIN ROOF TOP OUTDOOR AIR VENTILATION: | [6 empty] | 2009 IECC | SEER: | EER: |  | IECC Climate Zone: |  |  | 2012 IECC | SEER: | EER: | IECC Climate Zone: |  | 2015 IECC | SEER: | EER: | IECC Climate Zone: |  | 2018 IECC | SEER: | EER: | IECC Climate Zone: |  | 2019 CEC | SEER: | EER: | 1 | Doesn't Meet
A/C SIZE: | # OF A/C's: | VENTILATION TYPE: | VENTILATION RATE: | COOLING BTU: |  |  | HVAC SIZE: | SYSTEM CFM OUTPUT: | F.A.D. | C.R.V. | ECONOMIZER | HVAC HEAT STRIP BTHU CONV. |  | Bard AC | - | 9 | 1A | Not Required |  |  | Bard AC | - | 9 | 1A | Not Required | Bard AC | - | 9 | 1A | Not Required | Bard AC | - | 9 | 1A | Not Required | Bard AC | - | 11 | 2 | Doesn't Meet
3 TON | 0 | F.A.D. | 0 | 0 |  |  | N/A | 0 | 0 | 0 | 0 | ENTER KW: | 0 | Bard HP | - | 9 | 1B | Not Required |  |  | Bard HP | - | 9 | 1B | Not Required | Bard HP | - | 9 | 1B | Not Required | Bard HP | - | 9 | 1B | Not Required | Bard HP | - | 11 | 3 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  |  | 2 TON | 780 | 195 | 390 | 780 | = BTHU: | 0 | Roof Top AC (1P) | 13 | 11.18 | 2A | Not Required |  |  | Roof Top AC (1P) | 13 | 11.18 | 2A | No Exception | Roof Top AC (1P) | 14 | 11.76 | 2A | No Exception | Roof Top AC (1P) | 14 | 11.76 | 2A | Doesn't Meet | Roof Top AC (1P) | 14 | 11 | 4 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  |  | 2.5 TON | 900 | 225 | 450 | 900 |  |  | Roof Top AC (3P) | 13 | 11.18 | 2B | Doesn't Meet |  |  | Roof Top AC (3P) | 13 | 11.18 | 2B | Doesn't Meet | Roof Top AC (3P) | 14 | 11.76 | 2B | Doesn't Meet | Roof Top AC (3P) | 14 | 11.76 | 2B | Doesn't Meet | Roof Top AC (3P) | 14 | 11 | 5 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  |  | 3 TON | 1195 | 298.75 | 597.5 | 1195 |  |  | Roof Top HP (1P) | 13 | 11.18 | 3A | No Exception |  |  | Roof Top HP (1P) | 13 | 11.18 | 3A | No Exception | Roof Top HP (1P) | 14 | 11.76 | 3A | No Exception | Roof Top HP (1P) | 14 | 11.76 | 3A | Doesn't Meet | Roof Top HP (1P) | 14 | 11 | 6 | Doesn't Meet
N/A | 0 | F.A.D. | 0 | 0 |  |  | 3.5 TON | 1420 | 355 | 710 | 1420 | IECC ECONOMIZER REQUIREMENTS: |  | Roof Top HP (3P) | 13 | 11.18 | 3B |  |  |  | Roof Top HP (3P) | 13 | 11.18 | 3B | Doesn't Meet | Roof Top HP (3P) | 14 | 11.76 | 3B | Doesn't Meet | Roof Top HP (3P) | 14 | 11.76 | 3B | Doesn't Meet | Roof Top HP (3P) | 14 | 11 | 7 | Doesn't Meet
[7 empty] | 4 TON | 1605 | 401.25 | 802.5 | 1605 | 2009 | OVER 4.5 TON / > 300,00 BTU | Split System | 13 | 11.18 | 3C | No Exception |  |  | Split System | 13 | 11.18 | 3C | No Exception | Split System | 13 | 11.18 | 3C | No Exception | Split System | 13 | 11.18 | 3C | No Exception | Split System | 13 | 12.2 | 8 | Doesn't Meet
[7 empty] | 5 TON | 1800 | 450 | 900 | 1800 | 2012 | OVER 2.5 TON / > 300,000 BTU | Minisplit AC | 13 | 11.18 | 4A | No Exception |  |  | Minisplit AC | 13 | 11.18 | 4A | No Exception | Minisplit AC | 13 | 11.18 | 4A | No Exception | Minisplit AC | 13 | 11.18 | 4A | Doesn't Meet | Minisplit AC | 13 | 11.18 | 9 | Doesn't Meet
[7 empty] | 5 TON | 1700 | 425 | 850 | 1700 | 2015 | OVER 4.5 TON / > 300,00 BTU | Thru Wall | 12 | 10.56 | 4B | Doesn't Meet |  |  | Thru Wall | 12 | 10.56 | 4B | Doesn't Meet | Thru Wall | 12 | 10.56 | 4B | Doesn't Meet | Thru Wall | 12 | 10.56 | 4B | Doesn't Meet | Thru Wall | - | 9.3 | 10 | Doesn't Meet
[7 empty] | NOTE: THE ABOVE CFM OUTPUT IS BASED ON A DAIKEN HVAC UNIT. CFM OUTPUT MAY VARY BASED ON BRAND OF HVAC. |  |  |  |  | 2018 | OVER 4.5 TON / > 300,00 BTU | PTAC | - | 4.832 | 4C | No Exception |  |  | PTAC | - | 3 | 4C | No Exception | PTAC | - | 3.2 | 4C | No Exception | PTAC | - | 3.2 | 4C | No Exception | PTAC | - | 6.332 | 11 | Doesn't Meet
[17 empty] | 5A | No Exception | [5 empty] | 5A | No Exception |  |  |  | 5A | No Exception |  |  |  | 5A | No Exception |  |  |  | 12 | Doesn't Meet
OUTDOOR AIR PROPOSED: | TOTAL NEEDED: | ADD'L REQUIRED: | TOTAL COOLING BTU: | BTU REDUCTION BASED ON FRESH AIR TYPE: |  | VENTILATION REQUIREMENT: | [10 empty] | 5B | No Exception | [5 empty] | 5B | No Exception |  |  |  | 5B | No Exception |  |  |  | 5B | No Exception |  |  |  | 13 | Doesn't Meet
0 | 4250 | 4250 | 0 | 0 |  | NO ADD'L VENTILATION REQUIRED | [7 empty] | Meets Exception |  |  | 5C | No Exception |  |  | Doesn't Meet |  |  | 5C | No Exception | Doesn't Meet |  |  | 5C | No Exception | Doesn't Meet |  |  | 5C | No Exception | #REF! |  |  | 14 | Doesn't Meet
[6 empty] | Note: 2012 IECC: HVAC's 3-Ton or Greater require Economizers | [10 empty] | 6A | No Exception | [5 empty] | 6A | No Exception |  |  |  | 6A | No Exception |  |  |  | 6A | No Exception |  |  |  | 15 | Doesn't Meet
NOTES: | [16 empty] | 6B | No Exception | [5 empty] | 6B | No Exception |  |  |  | 6B | No Exception |  |  |  | 6B | No Exception |  |  |  | 16 | Doesn't Meet
1. WHEN ECONOMIZERS ARE REQUIRED OVER 300,000 BTU, LOOK AT CHART AND BRING THE TOTAL UNDER 300,000. NOT ALL HVAC'S NEED ECONOMIZERS. | [16 empty] | 7 | Not Required | [5 empty] | 7 | No Exception |  |  |  | 7 | Not in 2015 Code |  |  |  | 7 | Not in 2018 Code
2. WHEN CRV'S ARE REQUIRED, LOOK AT CHART AND MEET THE ADDITIONAL REQUIRED. NOT ALL HVAC'S NEED CRV'S IN CASES. | [16 empty] | 8 | Not Required | [5 empty] | 8 | No Exception |  |  |  | 8 | Not in 2015 Code |  |  |  | 8 | Not in 2018 Code
ECONOMIZER EXCEPTION
Code Year: | HVAC Size (Tons): | HVAC Type: | IECC Climate Zone: | Min. EER Rating: | Min. SEER Rating: | Equipment EER Rating: | Equipment SEER Rating: | Results: | [5 empty] | PMI Elec. Equip. |  | Equipment Size EER Rating
2018 IECC | 3 | Roof Top AC (1P) | 2B | 11.76 | 14 | 12.5 | 15 | Doesn't Meet | [7 empty] | 0.75 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5
[15 empty] | Bard AC | - | 11 | 11.3 | 11.2 | 11.2 | 11 | 11 | 11 | 11
[15 empty] | Bard HP | - | - | 11 | 11 | 11 | 11 | 11 | 11 | 11
[15 empty] | Roof Top AC (1P) | - | - | - | - | - | 12.5 | 12.5 | 12 | 12
[15 empty] | Roof Top AC (3P) | - | - | - | - | - | 13 | 13 | 12.5 | 12.5
[15 empty] | Roof Top HP (1P) | - | - | - | - | - | 13 | 13 | 12 | 12
[15 empty] | Roof Top HP (3P) | - | - | - | - | - | 13 | 13 | 12.5 | 12.5
[15 empty] | Minisplit AC | 10.4 | 10.6 | 12.2 | 9.2 | - | - | - | - | -
Split System
Thru Wall
PTAC
[14 empty] | PMI Elec. Equip. |  | Equipment Size SEER Rating
[16 empty] | 0.75 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 5
[15 empty] | Bard AC | - | - | - | - | - | - | - | - | -
[15 empty] | Bard HP | - | - | - | - | - | - | - | - | -
[15 empty] | Roof Top AC (1P) | - | - | - | - | - | 15 | 15 | 15 | 15
[15 empty] | Roof Top AC (3P) | - | - | - | - | - | 15 | 15 | 15 | 15
[15 empty] | Roof Top HP (1P) | - | - | - | - | - | 15.5 | 15.5 | 15 | 15
[15 empty] | Roof Top HP (3P) | - | - | - | - | - | 15 | 15 | 15 | 15
[15 empty] | Minisplit AC | 16 | 16 | 16 | 16 | - | - | - | - | -
Split System
Thru Wall
PTAC

## CA Outisde Air
2022 CEC / Table 120.1-A
BUILDING USE: | TOTAL OUTDOOR AIRFLOW RATE (Rt): | SQUARE FOOTAGE | OUTSIDE AIR REQUIRED | Notes:
Educational Facilities
Daycare (through age 4) | 0.21 |  | 0 |  | No | :Economizer, CRV, or ERV Installed
Daycare sickroom | 0.15 |  | 0
Classrooms (ages 5-8) | 0.38 |  | 0
Classrooms (ages 9-18) | 0.38 |  | 0
Lecture/postsecondary classroom | 0.38 |  | 0
Lecture hall (fixed seats) | -
Art classroom | 0.15 |  | 0
Science laboratories | 0.15 |  | 0
University/college laboratories | 0.15 |  | 0
Wood/metal shop | 0.15 |  | 0
Computer lab | 0.15 |  | 0
Media center | 0.15 |  | 0
Music/theater/dance | 1.07 |  | 0
Multiuse assembly | 0.5 |  | 0
Food and Beverage Service
Restaurant dining rooms | 0.5 |  | 0
Cafeteria/fast-food dining | 0.5 |  | 0
Bars, cocktail lounges | 0.5 |  | 0
Kitchen (cooking) | 0.15 |  | 0
General
Break rooms | 0.5 |  | 0
Coffee Stations | 0.5 |  | 0
Conference/meeting | 0.5 |  | 0
Corridors | 0.15 |  | 0
Occupiable storage rooms for liquids or gels | 0.15 |  | 0
Hotels, Motels, Resorts, Dormitories
Bedroom/living room | 0.15 |  | 0
Barracks sleeping areas | 0.15 |  | 0
Laundry rooms, central | 0.15 |  | 0
Laundry rooms within dwelling units | 0.15 |  | 0
Lobbies/pre-function | 0.5 |  | 0
Multipurpose assembly | 0.5 |  | 0
Office Buildings
Breakrooms | 0.5 |  | 0
Main entry lobbies | 0.5 |  | 0
Occupiable storage rooms for dry materials | 0.15 |  | 0
Office space | 0.15 |  | 0
Reception areas | 0.15 |  | 0
Telephone/data entry | 0.15 |  | 0
Miscellaneous Spaces
Bank vaults/safe deposit | 0.15 |  | 0
Banks or bank lobbies | 0.15 |  | 0
Computer (not printing) | 0.15 |  | 0
Freezer and refrigerated spaces (<50F) | -
General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  | 0
Pharmacy (prep. Area) | 0.15 |  | 0
Photo studios | 0.15 |  | 0
Shipping/receiving | 0.15 |  | 0
Sorting, packing, light assembly | 0.15 |  | 0
Telephone closets | 0.15 |  | 0
Transportation waiting | 0.5 |  | 0
Warehouses | 0.15 |  | 0
All others | 0.15 |  | 0
Public Assembly Spaces
Auditorium seating area | 1.07 |  | 0
Places of religious worship | 1.07 |  | 0
Courtrooms | 0.19 |  | 0
Legislative chambers | 0.19 |  | 0
Libraries (reading rooms and stack areas) | 0.15 |  | 0
Lobbies | 0.5 |  | 0
Museums (children's) | 0.25 |  | 0
Museums/galleries | 0.25 |  | 0
Residential
Common corridors | -
Retail
Sales (except as below) | 0.25 |  | 0
Mall common areas | 0.25 |  | 0
Barbershop | 0.4 |  | 0
Beauty and nail salons | 0.4 |  | 0
Pet shops (animal areas) | 0.25 |  | 0
Supermarket | 0.25 |  | 0
Coin-operated laundries | 0.3 |  | 0
Sports and Entertainment
Gym, sports arena (play area) | 0.5 |  | 0
Spetator areas | 0.5 |  | 0
Swimming (pool) | 0.15 |  | 0
Swimming (deck) | 0.5 |  | 0
Disco/dance floors | 1.5 |  | 0
Health club/aerobics room | 0.15 |  | 0
Health club/weight rooms | 0.15 |  | 0
Bowling alley (seating) | 1.07 |  | 0
Gambling casinos | 0.68 |  | 0
Game arcades | 0.68 |  | 0
Stages, studios | 0.5 |  | 0
|  | Total Oustide Air Required: | 0

## CA Vent Rate (hidden)
2019 CA ENERGY CODE: CHAPTER 3 / SECTION 120.1.2 (A) (B)
NOTE:
THERE ARE (2) METHODS OF FIGURING THE REQUIRED OUTSIDE AIR, BUT THE GREATER OF THE TWO MUST BE USED.
OVERALL BUILDING SQUARE FOOTAGE: | 0
TOTAL OCCUPANT LOAD: | 333.4 | <---- USE OCCUPANT CALCULATOR OR ENTER # OF OCCUPANTS, IF CELL IS OVERWRITTEN THEN USE FORMULA: =SUM('Occupant Calculator'!D27)
METHOD 1: OVERALL BUILDING SQ. FT.: | 0
METHOD 2: OVERALL OCCUPANCY: | 5001

## CA Endmount Calc
WALL MOUNT HVAC'S | [6 empty] | BARD WALL MOUNT OUTDOOR AIR VENTILATION:
A/C SIZE: | # OF A/C's: | VENTILATION TYPE: | VENTILATION RATE: | COOLING BTU: | CA ECONOMIZER REQUIREMENTS: |  | HVAC SIZE: | CFM OUTPUT: | F.A.D. | C.R.V. | ECONOMIZER | ERV | HVAC HEAT STRIP BTHU CONV. |  | 0
3 TON | 0 | F.A.D. | 0 | 0 | CA / UMC: | OVER 2.5 TON | N/A | 0 | 0 | 0 | 0 | 0 | ENTER KW: | 0
N/A | 0 | F.A.D. | 0 | 0 | Exception: ERV is provided, then no greater than 4 Ton |  | 1.5 TON | 600 | 150 | 300 | 600 | 250 | = BTHU: | 0
N/A | 0 | F.A.D. | 0 | 0 |  |  | 2 TON | 800 | 200 | 400 | 800 | 250
N/A | 0 | F.A.D. | 0 | 0 |  |  | 2.5 TON | 950 | 237.5 | 475 | 950 | 400
N/A | 0 | F.A.D. | 0 | 0 |  |  | 3 TON | 1150 | 287.5 | 575 | 1150 | 400
|  | NO ADD'L VENTILATION REQUIRED |  |  |  |  | 3.5 TON | 1350 | 337.5 | 675 | 1350 | 450
[7 empty] | 4 TON | 1550 | 387.5 | 775 | 1550 | 450
[7 empty] | 5 TON | 1750 | 437.5 | 875 | 1750 | 450
NOTE: THE ABOVE CFM OUTPUT IS BASED ON A BARD HVAC UNIT. CFM OUTPUT MAY VARY BASED ON BRAND OF HVAC.
OUTDOOR AIR PROPOSED: | TOTAL NEEDED: | ADD'L REQUIRED: | TOTAL COOLING BTU: | VENTILATION REQUIREMENT:
0 | 0 |  | 0 | NO ADD'L VENTILATION REQUIRED
NOTES:
1. WHEN MULTIPLE HVAC'S ARE SERVING COMMON A AREA(S) THEN SMOKE DUCT DETECTION WILL BE REQUIRED FOR THOSE HVAC'S.
2. WHEN CRV'S ARE REQUIRED, LOOK AT CHART AND MEET THE ADDITIONAL REQUIRED. NOT ALL HVAC'S NEED CRV'S IN SOME CASES.

## CA Rooftop Calc
RTU HVAC'S | [5 empty] | DAIKIN ROOF TOP OUTDOOR AIR VENTILATION:
A/C SIZE: | # OF A/C's: | FRESH AIR TYPE: | VENTILATION RATE: | COOLING BTU: |  | HVAC SIZE: | CFM OUTPUT: | F.A.D. | C.R.V. | ECONOMIZER | HVAC HEAT STRIP BTHU CONV.
3 TON | 1 | F.A.D. | 298.75 | 36,000 |  | N/A | 0 | 0 | 0 | 0 | ENTER KW: | 0
N/A | 0 | F.A.D. | 0 | 0 |  | 2 TON | 780 | 195 | 390 | 780 | = BTHU: | 0
N/A | 0 | F.A.D. | 0 | 0 |  | 2.5 TON | 900 | 225 | 450 | 900
N/A | 0 | F.A.D. | 0 | 0 |  | 3 TON | 1195 | 298.75 | 597.5 | 1195 | CA / UMC ECONOMIZER REQUIREMENTS:
N/A | 0 | F.A.D. | 0 | 0 |  | 3.5 TON | 1420 | 355 | 710 | 1420 | CA / UMC: | OVER 4.5 TON
[6 empty] | 4 TON | 1605 | 401.25 | 802.5 | 1605
[6 empty] | 5 TON | 1800 | 450 | 900 | 1800
[6 empty] | 5 TON | 1700 | 425 | 850 | 1700
NOTE: THE ABOVE CFM OUTPUT IS BASED ON A DAIKEN HVAC UNIT. CFM OUTPUT MAY VARY BASED ON BRAND OF HVAC.
OUTDOOR AIR PROPOSED: | TOTAL NEEDED: | ADD'L REQUIRED: | TOTAL COOLING BTU: | BTU REDUCTION BASED ON FRESH AIR TYPE: | VENTILATION REQUIREMENT:
298.75 | 0 | NO ADD'L NEEDED | 36000 | 36000 | NO ADD'L VENTILATION REQUIRED
NOTES:
1. WHEN MULTIPLE HVAC'S ARE SERVING COMMON A AREA(S) THEN SMOKE DUCT DETECTION WILL BE REQUIRED FOR THOSE HVAC'S.
2. WHEN CRV'S ARE REQUIRED, LOOK AT CHART AND MEET THE ADDITIONAL REQUIRED. NOT ALL HVAC'S NEED CRV'S IN CASES.

## Heating Climate Zones
HEATING BASED ON CLIMATE ZONE
[8 empty] | ZONE 1 | ZONE 2 | ZONE 3 | ZONE 4 | ZONE 5
ZONE 1 |  | ZONE 2 |  | ZONE 3 |  | ZONE 4 | ZONE 5 | 35 | 40 | 45 | 50 | 60
30-35 BTU's per sq. ft. |  | 35-40 BTU's per sq. ft. |  | 40-45 BTU's per sq. ft. |  | 45-50 BTU's per sq. ft. | 50-60 BTU's per sq. ft.
Pick Zone: | ZONE 5
Sq. Ft.: |  | Zone BTU
2000 | * | 60 | = | 35.172 | KW Heating
Note: The above zone BTU is based on the highest #. Adjust as needed.
If Cell C11 is overwritten, copy and paste the following formula (without the astrick):
*=INDEX(K3:O3,MATCH(B8,K2:O2,0))