## 2021-2024 Frontage Increase
2021-2024 IBC FRONTAGE INCREASE CALCULATOR | [6 empty] | Occupancy Classifications: |  | Fire Alarm Requirements:
[7 empty] | B: Business Group |  | B
Project #: | [6 empty] | B: Air Traffic Towers, Ambulatory Care (serving 6 or fewer), Banks, Barber/Beauty Shops, Vet Clinic, Bank, Offices, Outpatient Clinic, Education grade over 12th grade, food processing, print shops, radio/TV stations. |  | Combined occupant load of 500+, or 100+ above/below grade. Fire area contains an ambulatory care facility. Exception: Where a building is equipped with sprinkler system and occ. notification appliances activate throughout upon sprinkler water flow.
Notes:
Occupancy Classification: | B |  |  | 1 | Tubular per floor area limit per Table 506.2: | 9000
Construction Type: | V-B |  |  | 2 | Allowed height: | 40
Sprinkled: | NS |  |  |  | Allowed Stories: | 2
Number Of Stories: | 1 |  |  |  | Group R and NFPA 13R/D: | None
[5 empty] | NFPA 13 Sprinklers: | None
| Building Perimeter Lengths (Feet): |  | *Distance to property line or to far side of R.O.W. (feet): | 3 | Frontage Increase Factor: Table 506.3 |  | Notes: |  | Notes:
[5 empty] | Perimeter, (P): | 168 | 1 | See Chapter 3 for Occupancy Classifications. | 1 | See Section 907 for Fire Alarm requirements.
[5 empty] | Frontage perimeter, (F): | 168
Facing North (Ft): | 60 |  | 30 |  | Percentage of perimeter > 20': | 100% | CONSTRUCTION TYPES:
[5 empty] | Minimum distance (W): | 24 | V-B |  | Sprinkler Types:
[5 empty] | Frontage Increase Factor (If): | 0.5 | All exterior and interior walls made of combustible material. Type B requires no rating of structural framing / elements. |  | NS
|  |  |  | 4 | Allowable per story area, Aa = At+(NS x If): | 13500 |  |  | NS: Non Sprinkled
Facing East (Ft): | 24 |  | 35 | 5 | Maximum allowable area, Aa=[At+(NSxIf)]xSa: | 13500
Special Conditions:
|  |  |  | 1 | Unlimited area reduction in public ways or yard allowed (60' to 40'). Restrictions apply. Section 507.
Facing South (Ft): | 60 |  | 24
|  |  |  | 2 | Unlimited area allowed with 1-Story (non-sprinkled), Groups F-2 or S-2 with public ways or yards not less than 60' on all sides. Section 507.3. |  | Notes:
[7 empty] | 1 | Type A construction referes to "Protected" (rated) construction, except with Type I structures.
Facing West (Ft): | 24 |  | 60 | 3 | Unlimited area allowed with 1-Story (NFPA-13 sprinkled), Groups A-4 (other than type V) or B, F, M or S with public ways or yards not less than 60' on all sides. Section 507.4.
[7 empty] | 2 | Type B construction referes to "Unprotected" (non-rated) construction, except with Type I structures.
|  |  |  | 4 | Sprinklers required for all Group R occupancies. Certain R occupancies / conditions allow for an NFPA 13D system. Section 903.2.8.
[7 empty] | 3 | See Table 601 for fire resistance requirements.
Allowable area per floor (Aa=[At+(NSxIf)]: | 13500 | Sq. Ft. per floor |  | 5 | Type V-A construction requires all structural elements / members be 1-hour rated (Ext. Walls, floors, roof, ridge beams, and columns). Table 601.
Total allowable area [Aa x # of Stories]: | 13500 | Sq. Ft. total |  |  |  |  | 4 | See Table 705.5 for fire resistance requirements for exterior walls based on seperation distance.
Max. allowable Height (Table 504.3): | 40 | Feet
Max. Allowable Stories (Aa=[At+(NSxIf)]xSa: | 2 | Storie(s) |  | 6 | See Table 705.5 for fire rating requirements for exterior walls based on seperation distance.
Allowed Area Increase Multi-Story (CA only): | No Limitations | Sq. Ft. each story
Allowed Height W/ Area Increase (CA only): | 40 | Feet total |  | 7 | Multi-Story not to exceed 3 without sprinkler system. See Section 506.2.3.
Allowed Stories W/ Area Increase (CA only): | No Limitations | Storie(s)
|  |  |  | 8 | To qualify for area factor increase based on frontage, at least 25% of the building perimeter on public way / space shall have min. width of 20'. Section 506.3.1.
PROPERTY LINE EXAMPLE: |  |  | (R.O.W.=Right Of Way)
Note: Per section 506.3.2, the smallest public way or open space must be used.

## 2009-2018 Frontage Increase
2009 - 2018 IBC FRONTAGE INCREASE CALCULATOR | [6 empty] | Occupancy Classifications: |  | Fire Alarm Requirements:
[7 empty] | B: Business Group |  | B
Project #: | [6 empty] | B: Air Traffic Towers, Ambulatory Care (serving 6 or fewer), Banks, Barber/Beauty Shops, Vet Clinic, Bank, Offices, Outpatient Clinic, Education grade over 12th grade, food processing, print shops, radio/TV stations. |  | Combined occupant load of 500+, or 100+ above/below grade. Fire area contains an ambulatory care facility. Exception: Where a building is equipped with sprinkler system and occ. notification appliances activate throughout upon sprinkler water flow.
Notes:
Occupancy Classification: | B |  |  | 1 | Tubular per floor area limit per Table 506.2: | 9000
Construction Type: | V-B |  |  | 2 | Allowed height: | 40
Sprinkled: | NS |  |  |  | Allowed Stories: | 2
Number Of Stories: | 1 |  |  |  | Group R and NFPA 13R/D: | None
[5 empty] | NFPA 13 Sprinklers: | None
| Building Perimeter Lengths (Feet): |  | *Distance to property line or to far side of R.O.W. (feet): | 3 | Frontage Increase: If=[F/P - 0.25]W/30 |  | Notes: |  | Notes:
[5 empty] | Frontage coefficient, (If): | 0.32407 | 1 | See Chapter 3 for Occupancy Classifications. | 1 | See Section 907 for Fire Alarm requirements (2018 IBC / 2019 CBC).
[5 empty] | Perimeter, (P): | 300
Facing North (Ft): | 120 |  | 18 |  | Frontage perimeter, (F): | 180 | CONSTRUCTION TYPES:
[5 empty] | Average frontage distance (W): | 27.7778 | V-B |  | Sprinkler Types:
|  |  |  | 4 | Allowable per story area, Aa = At+(NS x If): | 11916.6667 | All exterior and interior walls made of combustible material. Type B requires no rating of structural framing / elements. |  | NS
|  |  |  | 5 | Maximum allowable area, Aa=[At+(NSxIf)]xSa: | 11916.6667 |  |  | NS: Non Sprinkled
Facing East (Ft): | 80 |  | 50
Special Conditions:
|  |  |  | 1 | Unlimited area reduction in public ways or yard allowed (60' to 40'). Restrictions apply. Section 507.2 (2018 IBC / 2019 CBC)
Facing South (Ft): | 60 |  | 40 | 2 | Unlimited area allowed with 1-Story (non-sprinkled), Groups F-2 or S-2 with public ways or yards not less than 60' on all sides. Section 507.3 (2018 IBC / 2019 CBC)
Notes:
[7 empty] | 1 | Type A construction referes to "Protected" (rated) construction, except with Type I structures.
|  |  |  | 3 | Unlimited area allowed with 1-Story (sprinkled), Groups A-4 (other than type V) A-3, B, F, M or S with public ways or yards not less than 60' on all sides. Section 507.4 (2018 IBC / 2019 CBC)
Facing West (Ft): | 40 |  | 20
[7 empty] | 2 | Type B construction referes to "Unprotected" (non-rated) construction, except with Type I structures.
|  |  |  | 4 | Sprinklers required for all Group R occupancies. Certain R occupancies / conditions allow for an NFPA 13D system (See sub-sections). Section 903.2.8 (2018 IBC / 2019 CBC)
|  |  |  | 5 | Type V-A construction requires all structural elements / members be 1-hour rated (Ext. Walls, floors, roof, ridge beams, and columns). Table 601. |  | 3 | See Table 601 for fire resistance requirements.
Allowable area per floor (Aa=[At+(NSxIf)]: | 11916.6667 | Sq. Ft. per floor
Total allowable area [Aa x # of Stories]: | 11916.6667 | Sq. Ft. total |  |  |  |  | 4 | See Table 602 for fire resistance requirements for exterior walls based on seperation distance.
Max. allowable Height (Table 504.3): | 40 | Feet |  | 6 | See Table 602 for fire rating requirements for exterior walls based on seperation distance.
Max. Allowable Stories (Aa=[At+(NSxIf)]xSa: | 2 | Storie(s)
Allowed Area Increase Multi-Story (CA only): | No Limitations | Sq. Ft. each story |  | 7 | Multi-Story not to exceed 3 without sprinkler system. See Section 506.2.3 (2018 IBC / 2019 CBC)
Allowed Height W/ Area Increase (CA only): | 40 | Feet total
Allowed Stories W/ Area Increase (CA only): | No Limitations | Storie(s) |  | 8 | To qualify for area factor increase based on frontage, at least 25% of the building perimeter on public way / space shall have min. width of 20'. Section 506.3.1 (2018 IBC / 2019 CBC)
PROPERTY LINE EXAMPLE: |  |  | (R.O.W.=Right Of Way)

## 2021-2024 Mixed Occupancy
2021-2024 IBC MIXED OCCUPANCY SINGLE STORY | [7 empty] | CONSTRUCTION TYPES: |  | Sprinkler Types:
[8 empty] | V-B |  | NS
Project #: | [7 empty] | All exterior and interior walls made of combustible material. Type B requires no rating of structural framing / elements. |  | NS: Non Sprinkled
| OCCUPANCY 1 |  | OCCUPANCY 2 | Notes:
Occupancy Classification: | B |  | E | 1 | Tubular per floor area limit per Table 506.2: | 9000 | 9500
Construction Type: | V-B |  |  |  | Group R and NFPA 13R/D: | None | None
Sprinkled: | NS |  |  |  | NFPA 13 Sprinklers: | None | None
|  |  |  | 3 | Frontage Increase Factor: Table 506.3
[5 empty] | Perimeter, (P): | 168 | 168
| Building Perimeter Lengths (Feet): |  | *Distance to property line or to far side of R.O.W. (feet): |  | Frontage perimeter, (F): | 168 | 168 | Notes:
[5 empty] | Percentage of perimeter > 20': | 100% | 100% | 1 | Type A construction referes to "Protected" (rated) construction, except with Type I structures.
[5 empty] | Minimum distance (W): | 20 | 20
Facing North (Ft): | 60 |  | 20 |  | Frontage Increase Factor (If): | 0.5 | 0.5
[5 empty] | Allowable per story area, Aa = At+(NS x If): | 13500 | 14250 | 2 | Type B construction referes to "Unprotected" (non-rated) construction, except with Type I structures.
Special Conditions:
Facing East (Ft): | 24 |  | 30 | 1 | See Section 507.4 for mixed-occupancy, single story buildings. |  |  | 3 | See Table 601 for fire resistance requirements.
|  |  |  | 2 | See Section 507.8 for Group H-2, H-3, and Group H-3 restrictions. |  |  | 4 | See Table 705.5 for fire resistance requirements for exterior walls based on seperation distance.
Facing South (Ft): | 60 |  | 30 | 3 | See Table 508.4 for occupancy seperation requirements (Ratings) as applicable.
|  |  |  | 4 | To qualify for area factor increase based on frontage, at least 25% of the building perimeter on public way / space shall have min. width of 20'. Section 506.3.2.
Facing West (Ft): | 24 |  | 30
| SQ. FT. OF OCC. 1 | SQ. FT. OF OCC. 2
Square Footage of Area(s): | 0 | 0
Max. occupancy area, Aa = At+(NS x If): | 13500 | 14250
Occupancy W/O Area Increase: | 9000 | 9500
W/ Area Increase (Sq. Ft./Aa 1) + (Sq. Ft./Aa 2): | 0 | < 1 THEREFORE OK
W/O Area Increase (Sq. Ft./Aa 1) + (Sq. Ft./Aa 2): | 0 | < 1 THEREFORE OK

## 2009-2018 Mixed Occupancy
2009 - 2018 IBC MIXED OCCUPANCY SINGLE STORY | [7 empty] | CONSTRUCTION TYPES: |  | Sprinkler Types:
[8 empty] | V-B |  | NS
Project #: | [7 empty] | All exterior and interior walls made of combustible material. Type B requires no rating of structural framing / elements. |  | NS: Non Sprinkled
| OCCUPANCY 1 |  | OCCUPANCY 2 | Notes:
Occupancy Classification: | B |  | E | 1 | Tubular per floor area limit per Table 506.2: | 9000 | 9500
Construction Type: | V-B |  |  |  | Group R and NFPA 13R/D: | None | None
Sprinkled: | NS |  |  |  | NFPA 13 Sprinklers: | None | None
|  |  |  | 3 | Area increase: If=[F/P - 0.25]W/30
[5 empty] | Frontage coefficient, (If): | 0.5 | 0.5
| Building Perimeter Lengths (Feet): |  | *Distance to property line or to far side of R.O.W. (feet): |  | Perimeter, (P): | 168 | 168 | Notes:
[5 empty] | Frontage perimeter, (F): | 168 | 168 | 1 | Type A construction referes to "Protected" (rated) construction, except with Type I structures.
[5 empty] | Average frontage distance (W): | 20 | 20
Facing North (Ft): | 60 |  | 20 | 4 | Maximum allowable area, Aa = At+(NS x If): | 13500 | 14250
[8 empty] | 2 | Type B construction referes to "Unprotected" (non-rated) construction, except with Type I structures.
Special Conditions:
Facing East (Ft): | 24 |  | 20 | 1 | See Section 506.2.2 for mixed-occupancy, single story buildings. (2018 IBC / 2019 CBC) |  |  | 3 | See Table 601 for fire resistance requirements.
|  |  |  | 2 | See Section 506.2.2.1 for Group H-2 and Group H-3 restrictions. (2018 IBC / 2019 CBC) |  |  | 4 | See Table 602 for fire resistance requirements for exterior walls based on seperation distance.
Facing South (Ft): | 60 |  | 20 | 3 | See Table 508.4 for occupancy seperation requirements (Ratings) (2018 IBC / 2019 CBC)
|  |  |  | 4 | To qualify for area factor increase based on frontage, atleast 25% of the building perimeter on public way / space shall have min. width of 20'. Section 506.3.1 (2018 IBC / 2019 CBC)
Facing West (Ft): | 24 |  | 20
| SQ. FT. OF OCC. 1 | SQ. FT. OF OCC. 2
Square Footage of Area(s): | 0 | 0
Max. occupancy area, Aa = At+(NS x If): | 13500 | 14250
Occupancy W/O Area Increase: | 9000 | 9500
W/ Area Increase (Sq. Ft./Aa 1) + (Sq. Ft./Aa 2): | 0 | < 1 THEREFORE OK
W/O Area Increase (Sq. Ft./Aa 1) + (Sq. Ft./Aa 2): | 0 | < 1 THEREFORE OK

## 2021 Bldg Ht Table 504.3 (hidden)
NOT SPRINKLED | [12 empty] | SPRINKLERS (S1 & SM) | [12 empty] | AREA INCREASE LIMITATIONS | [12 empty] | S13D SPRINKLERS | [12 empty] | S13R SPRINKLERS
| I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B
A-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-1 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | A-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-2 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | A-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-3 | UL | 160 | 65 | 55 | 65 | 55 | 270 | 180 | 85 | 85 | 50 | 40 | A-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-3 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-3 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-4 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | A-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-4 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-4 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-5 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | A-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | A-5 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-5 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
B | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | B | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | B | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | B | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | B | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
E | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | E | UL | 160 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | E | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | E | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | E | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
F-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | F-1 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | F-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | F-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | F-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
F-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | F-2 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | F-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | F-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | F-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-1 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-1 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-1 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-2 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-2 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-2 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-3 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-3 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-3 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-3 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-3 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | H-4 | UL | 180 | 85 | 75 | 85 | 75 | 140 | 100 | 85 | 85 | 70 | 60 | H-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | H-4 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-4 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-5 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-5 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-5 | UL | 160 | 65 | 55 | 65 | 55 | 120 | 90 | 65 | 65 | 50 | 40 | H-5 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-5 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-1 Cond. 1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-1 Cond. 1 | UL | 180 | 85 | 75 | 85 | 75 | 180 | 120 | 85 | 85 | 70 | 60 | I-1 Cond. 1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-1 Cond. 1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-1 Cond. 1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
I-1 Cond. 2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-1 Cond. 2 | UL | 180 | 85 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-1 Cond. 2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-1 Cond. 2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-1 Cond. 2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-2/I-2.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-2/I-2.1 | UL | 180 | 85 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-2/I-2.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-2/I-2.1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-2/I-2.1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-3 | UL | 180 | 85 | 75 | 85 | 75 | 180 | 120 | 85 | 85 | 70 | 60 | I-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-3 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-3 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | I-4 | UL | 180 | 85 | 75 | 85 | 75 | 180 | 120 | 85 | 85 | 70 | 60 | I-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 50 | I-4 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-4 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
L | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | L | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | L | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | L | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | L | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
M | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | M | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | M | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | M | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | M | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
R-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | R-1 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | R-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | R-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | R-1 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 60 | 60 | 60 | 50 | 40
R-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | R-2 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | R-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 60 | 40 | R-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | R-2 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 60 | 60 | 60 | 50 | 40
R-2.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | R-2.1 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | R-2.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | R-2.1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 40 | R-2.1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
R-2.2 (CA Only) | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | R-2.2 (CA Only) | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | R-2.2 (CA Only) | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 60 | 40 | R-2.2 (CA Only) | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | R-2.2 (CA Only) | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
R-3/R-3.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | R-3/R-3.1 | UL | 160 | 65 | 55 | 65 | 55 | 270 | 180 | 85 | 85 | 50 | 40 | R-3/R-3.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | R-3/R-3.1 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 60 | 60 | 60 | 50 | 40 | R-3/R-3.1 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 60 | 60 | 60 | 50 | 40
R-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | R-4 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | R-4 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | R-4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 40 | R-4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
S-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | S-1 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | S-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | S-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | S-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
S-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | S-2 | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | S-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | S-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | S-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
U | UL | 160 | 65 | 55 | 65 | 55 | 65 | 65 | 65 | 65 | 50 | 40 | U | UL | 180 | 85 | 75 | 85 | 75 | 270 | 180 | 85 | 85 | 70 | 60 | U | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | U | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | U | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
40 | [12 empty] | 60 | [12 empty] | No Limitations | [12 empty] | NP W/13D | [12 empty] | NP W/ 13R
DO NOT OVERIDE BELOW
B | V-B
Note: UL = Unlimited; NP = Not Permitted;
For SI: 1 square foot = 304.8 mm
NS = Buildings not equipped throughout with an automatic sprinkler system.
S = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
S13R = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2
S13D = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.3.

## 2021 Stories Table 504.4 (hidden)
NOT SPRINKLED | [13 empty] | SPRINKLED (S1 & SM) | [13 empty] | AREA INCREASE LIMITATIONS | [13 empty] | SPRINKLED 13D | [13 empty] | SPRINKLED 13R
| I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B
A-1 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | NS | A-1 | UL | 6 | 4 | 3 | 4 | 3 | 9 | 6 | 4 | 4 | 3 | 2 | S (without area increase) | A-1 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | S (with area increase) | A-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-2 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | NS | A-2 | UL | 12 | 4 | 3 | 4 | 3 | 18 | 12 | 6 | 4 | 3 | 2 | S (without area increase) | A-2 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | S (with area increase) | A-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-3 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | NS | A-3 | UL | 12 | 4 | 3 | 4 | 3 | 18 | 12 | 6 | 4 | 3 | 2 | S (without area increase) | A-3 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | S (with area increase) | A-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-4 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | NS | A-4 | UL | 12 | 4 | 3 | 4 | 3 | 18 | 12 | 6 | 4 | 3 | 2 | S (without area increase) | A-4 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | S (with area increase) | A-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-5 | UL | UL | UL | UL | UL | UL | 1 | 1 | 1 | UL | UL | UL | NS | A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | S | A-5 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
B | UL | 11 | 5 | 3 | 5 | 3 | 5 | 5 | 5 | 5 | 3 | 2 | NS | B | UL | 12 | 6 | 4 | 6 | 4 | 18 | 12 | 9 | 6 | 4 | 3 | S | B | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | B | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | B | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
E | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 1 | 1 | NS | E | UL | 6 | 4 | 3 | 4 | 3 | 9 | 6 | 4 | 4 | 2 | 2 | S (without area increase) | E | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 1 | 1 | S (with area increase) | E | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | E | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-1 | UL | 11 | 4 | 2 | 3 | 2 | 3 | 3 | 3 | 4 | 2 | 1 | NS | F-1 | UL | 12 | 5 | 3 | 4 | 3 | 10 | 7 | 5 | 5 | 3 | 2 | S | F-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-2 | UL | 11 | 5 | 3 | 4 | 3 | 5 | 5 | 5 | 5 | 3 | 2 | NS | F-2 | UL | 12 | 6 | 4 | 5 | 4 | 12 | 8 | 6 | 6 | 4 | 3 | S | F-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-1 | 1 | 1 | 1 | 1 | 1 | 1 | NP | NP | NP | 1 | 1 | NP W/ V-B Construction | NS | H-1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | NP W/ V-B Construction | S | H-1 | 1 | 1 | 1 | 1 | 1 | 1 | NP | NP | NP | 1 | 1 | NP W/ V-B Construction |  | H-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ V-B Construction |  | H-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ V-B Construction
H-2 | 20 | 3 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | NP W/ V-B Construction | NS | H-2 | 20 | 3 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | S | H-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-3 | 20 | 6 | 4 | 2 | 4 | 2 | 3 | 3 | 3 | 4 | 2 | 1 | NS | H-3 | 20 | 6 | 4 | 2 | 4 | 2 | 4 | 4 | 4 | 4 | 2 | 1 | S | H-3 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-4 | 20 | 7 | 5 | 3 | 5 | 3 | 5 | 5 | 5 | 5 | 3 | 2 | NS | H-4 | 20 | 8 | 6 | 4 | 6 | 4 | 8 | 7 | 6 | 6 | 4 | 3 | S (without area increase) | H-4 | 20 | 7 | 5 | 3 | 5 | 3 | 5 | 5 | 5 | 5 | 3 | 2 | S (with area increase) | H-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-5 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 3 | 3 | 2 | NS | H-5 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | S | H-5 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-1 Cond. 1 | UL | 9 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | NS | I-1 Cond. 1 | UL | 10 | 5 | 4 | 5 | 4 | 10 | 7 | 5 | 5 | 4 | 3 | S | I-1 Cond. 1 | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NS | I-1 Cond. 1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 1 | UL | 9 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | S13R
I-1 Cond. 2 | UL | 9 | 4 | 3 | 4 | 3 | 3 | 3 | 3 | 4 | 3 | 2 | NS | I-1 Cond. 2 | UL | 10 | 5 | 3 | 4 | 3 | 10 | 6 | 4 | 4 | 3 | 2 | S | I-1 Cond. 2 | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NS | I-1 Cond. 2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-2/I-2.1 | UL | 4 | 2 | 1 | 1 | NP W/ III-B or V-B Construction | NP | NP | NP | 1 | 1 | NP W/ III-B or V-B Construction | NS | I-2/I-2.1 | UL | 5 | 3 | 1 | 1 | NP W/ III-B or V-B Construction | 7 | 5 | 1 | 1 | 1 | NP W/ III-B or V-B Construction | S (without area increase) | I-2/I-2.1 | UL | 4 | 2 | 1 | 1 | NP W/ III-B or V-B Construction | NP | NP | NP | 1 | 1 | NP W/ III-B or V-B Construction | S (with area increase) | I-2/I-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ III-B or V-B | NP W/ III-B or V-B | NP W/ III-B or V-B | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-2/I-2.1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ III-B or V-B | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-3 | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP / Use I-A or I-B Construction | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NS | I-3 | UL | 5 | 3 | 2 | 3 | 2 | 7 | 5 | 3 | 3 | 3 | 2 | S (without area increase) | I-3 | UL | 2 | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | S (with area increase) | I-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-4 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 1 | 1 | NS | I-4 | UL | 6 | 4 | 3 | 4 | 3 | 9 | 6 | 4 | 4 | 2 | 2 | S (without area increase) | I-4 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 3 | 1 | 1 | S (with area increase) | I-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
L | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NS | L | 20 | 6 | 5 | 3 | 5 | 3 | 5 | 5 | 5 | 5 | 3 | 2 | S | L | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | L | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | L | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
M | UL | 11 | 4 | 2 | 4 | 2 | 4 | 4 | 4 | 4 | 3 | 1 | NS | M | UL | 12 | 5 | 3 | 5 | 3 | 12 | 8 | 6 | 5 | 4 | 2 | S | M | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | M | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | M | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | NS | R-1 | UL | 12 | 5 | 5 | 5 | 5 | 18 | 12 | 8 | 5 | 4 | 3 | S (without area increase) | R-1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | S (with area increase) | R-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | S13R
R-2 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | NS | R-2 | UL | 12 | 5 | 5 | 5 | 5 | 18 | 12 | 8 | 5 | 4 | 3 | S (without area increase) | R-2 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | S (with area increase) | R-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | S13R
R-2.2 (CA Only) | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NS | R-2.2 (CA Only) | UL | 12 | 5 | 5 | 5 | 5 | 5 | 12 | 5 | 5 | 4 | 3 | S (without area increase) | R-2.2 (CA Only) | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | S (with area increase) | R-2.2 (CA Only) | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2.2 (CA Only) | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-2.1 | UL | 6 | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NS | R-2.1 | UL | 6 | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | S | R-2.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | R-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ 13D | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ 13D | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction |  | R-2.1 | UL | 4 | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-A, IV-B, IV-C, IV-HT, V-B Construction | S13R
R-3/R-3.1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | NS | R-3/R-3.1 | UL | 12 | 5 | 5 | 5 | 5 | 4 | 12 | 5 | 5 | 4 | 4 | S | R-3/R-3.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | R-3/R-3.1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | S13D | R-3/R-3.1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | S13R
R-4 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | NS | R-4 | UL | 11 | 5 | 5 | 5 | 5 | 4 | 12 | 5 | 5 | 4 | 3 | S | R-4 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | R-4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | S13D | R-4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | S13R
S-1 | UL | 11 | 4 | 2 | 3 | 2 | 4 | 4 | 4 | 4 | 3 | 1 | NS | S-1 | UL | 12 | 5 | 3 | 4 | 3 | 10 | 7 | 5 | 5 | 4 | 2 | S | S-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
S-2 | UL | 11 | 5 | 3 | 4 | 3 | 4 | 4 | 4 | 5 | 4 | 2 | NS | S-2 | UL | 12 | 6 | 4 | 5 | 4 | 12 | 8 | 5 | 6 | 5 | 3 | S | S-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
U | UL | 5 | 4 | 2 | 3 | 2 | 4 | 4 | 4 | 4 | 2 | 1 | NS | U | UL | 6 | 5 | 3 | 4 | 3 | 9 | 6 | 5 | 5 | 3 | 2 | S | U | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | U | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | U | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
2 | [13 empty] | 3 | [13 empty] | No Limitations | [13 empty] | NP W/ 13D | [13 empty] | NP W/13R
DO NOT OVERIDE BELOW
B | V-B
Note: UL = Unlimited; NP = Not Permitted;
NS = Buildings not equipped throughout with an automatic sprinkler system.
S = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
S13R = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2
S13D = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.3.

## 2021 area Table 506.2 (hidden)
NOT SPRINKLED | [14 empty] | SPRINKLED (S1) | [13 empty] | SPRINKLED MULTI-STORY (SM) | [13 empty] | AREA INCREASE LIMITATIONS | [13 empty] | SPRINKLED 13D | [13 empty] | SPRINKLED 13R
| I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-A | IV-B | IV-C | IV-HT | V-A | V-B
A-1 | UL | UL | 15500 | 8500 | 14000 | 8500 | 45000 | 30000 | 18750 | 15000 | 11500 | 5500 | NS |  | A-1 | UL | UL | 62000 | 34000 | 56000 | 34000 | 180000 | 120000 | 75000 | 60000 | 46000 | 22000 | S1 | A-1 | UL | UL | 46500 | 25500 | 42000 | 25500 | 135000 | 90000 | 56250 | 45000 | 34500 | 16500 | SM | A-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-2 | UL | UL | 15500 | 9500 | 14000 | 9500 | 45000 | 30000 | 18750 | 15000 | 11500 | 6000 | NS |  | A-2 | UL | UL | 62000 | 38000 | 56000 | 38000 | 180000 | 120000 | 75000 | 60000 | 46000 | 24000 | S1 | A-2 | UL | UL | 46500 | 28500 | 42000 | 28500 | 135000 | 90000 | 56250 | 45000 | 34500 | 18000 | SM (without ht. increase) | A-2 | UL | UL | 15500 | 9500 | 14000 | 95000 | 45000 | 30000 | 18750 | 15000 | 11500 | 6000 | SM (with ht. increase) | A-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-3 | UL | UL | 15500 | 9500 | 14000 | 9500 | 45000 | 30000 | 18750 | 15000 | 11500 | 6000 | NS | 0 | A-3 | UL | UL | 62000 | 38000 | 56000 | 38000 | 180000 | 120000 | 75000 | 60000 | 46000 | 24000 | S1 | A-3 | UL | UL | 46500 | 28500 | 42000 | 28500 | 135000 | 90000 | 56250 | 45000 | 34500 | 18000 | SM | A-3 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-4 | UL | UL | 15500 | 9500 | 14000 | 9500 | 45000 | 30000 | 18750 | 15000 | 11500 | 6000 | NS |  | A-4 | UL | UL | 62000 | 38000 | 56000 | 38000 | 180000 | 120000 | 75000 | 60000 | 46000 | 24000 | S1 | A-4 | UL | UL | 46500 | 28500 | 42000 | 28500 | 135000 | 90000 | 56250 | 45000 | 34500 | 18000 | SM (without ht. increase) | A-4 | UL | UL | 15500 | 9500 | 14000 | 9500 | 45000 | 30000 | 18750 | 15000 | 11500 | 6000 | SM (with ht. increase) | A-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | NS |  | A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | S1 | A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | SM | A-5 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
B | UL | UL | 37500 | 23000 | 28500 | 19000 | 108000 | 72000 | 45000 | 36000 | 18000 | 9000 | NS |  | B | UL | UL | 150000 | 92000 | 114000 | 76000 | 432000 | 288000 | 180000 | 144000 | 72000 | 36000 | S1 | B | UL | UL | 112500 | 69000 | 85500 | 57000 | 324000 | 216000 | 135000 | 108000 | 54000 | 27000 | SM | B | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | B | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | B | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
E | UL | UL | 26500 | 14500 | 23500 | 14500 | 76500 | 51000 | 31875 | 25500 | 18500 | 9500 | NS |  | E | UL | UL | 106000 | 58000 | 94000 | 58000 | 306000 | 204000 | 127500 | 102000 | 74000 | 38000 | S1 | E | UL | UL | 79500 | 43500 | 70500 | 43500 | 229500 | 153000 | 95625 | 76500 | 55500 | 28500 | SM (without ht. increase) | E | UL | UL | 26500 | 14500 | 23500 | 14500 | 76500 | 51000 | 37875 | 25500 | 18500 | 9500 | SM (with ht. increase) | E | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | E | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-1 | UL | UL | 25000 | 15500 | 19000 | 12000 | 100500 | 67000 | 41875 | 33500 | 1400 | 8500 | NS |  | F-1 | UL | UL | 100000 | 62000 | 76000 | 48000 | 402000 | 268000 | 167500 | 134000 | 56000 | 34000 | S1 | F-1 | UL | UL | 75000 | 46500 | 57000 | 36000 | 301500 | 201000 | 125625 | 100500 | 42000 | 25500 | SM | F-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-2 | UL | UL | 37500 | 23000 | 28500 | 18000 | 151500 | 101000 | 63125 | 50500 | 21000 | 13000 | NS |  | F-2 | UL | UL | 150000 | 92000 | 114000 | 72000 | 606000 | 404000 | 252500 | 202000 | 84000 | 52000 | S1 | F-2 | UL | UL | 112500 | 69000 | 85500 | 54000 | 454500 | 303000 | 189375 | 151500 | 63000 | 39000 | SM | F-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-1 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 10500 | 10500 | 10500 | 7500 | NP W/ V-B Construction | NS |  | H-1 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 10500 | 10500 | 10500 | 7500 | NP W/ V-B Construction | S1 | H-1 | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP | H-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ V-B Construction |  | H-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ V-B Construction
H-2 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 10500 | 10500 | 10500 | 7500 | 3000 | NS |  | H-2 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 10500 | 10500 | 10500 | 7500 | 3000 | S1 | H-2 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 10500 | 10500 | 10500 | 7500 | 3000 | SM | H-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-3 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25500 | 25500 | 25500 | 25500 | 10000 | 5000 | NS |  | H-3 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25500 | 25500 | 25500 | 25500 | 10000 | 5000 | S1 | H-3 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25500 | 25500 | 25500 | 25500 | 10000 | 5000 | SM | H-3 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-4 | UL | UL | 37500 | 17500 | 28500 | 17500 | 72000 | 54000 | 40500 | 36000 | 18000 | 6500 | NS |  | H-4 | UL | UL | 150000 | 70000 | 114000 | 70000 | 288000 | 216000 | 162000 | 144000 | 72000 | 26000 | S1 | H-4 | UL | UL | 112500 | 52500 | 85500 | 52500 | 216000 | 162000 | 121500 | 108000 | 54000 | 19500 | SM (without ht. increase) | H-4 | UL | UL | 37500 | 17500 | 28500 | 17500 | 72000 | 54000 | 40500 | 36000 | 18000 | 6500 | SM (with ht. increase) | H-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-5 | UL | UL | 37500 | 23000 | 28500 | 19000 | 72000 | 54000 | 40500 | 36000 | 18000 | 9000 | NS |  | H-5 | UL | UL | 150000 | 92000 | 114000 | 76000 | 288000 | 216000 | 162000 | 144000 | 72000 | 36000 | S1 | H-5 | UL | UL | 112500 | 69000 | 85500 | 57000 | 216000 | 162000 | 121500 | 10800 | 54000 | 27000 | SM (without ht. increase) | H-5 | UL | UL | 37500 | 23000 | 28500 | 19000 | 72000 | 54000 | 40500 | 36000 | 18000 | 9000 | SM (with ht. increase) | H-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-1 Cond. 1 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 54000 | 36000 | 18000 | 18000 | 10500 | 4500 | NS |  | I-1 Cond. 1 | UL | 220000 | 76000 | 40000 | 66000 | 40000 | 216000 | 144000 | 72000 | 72000 | 42000 | 18000 | S1 | I-1 Cond. 1 | UL | 165000 | 57000 | 30000 | 49500 | 30000 | 162000 | 108000 | 54000 | 54000 | 31500 | 13500 | SM | I-1 Cond. 1 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 54000 | 36000 | 18000 | 18000 | 10500 | 4500 |  | I-1 Cond. 1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 1 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 54000 | 36000 | 18000 | 18000 | 10500 | 4500 | S13R
I-1 Cond. 2 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 54000 | 36000 | 18000 | 18000 | 10500 | 4500 | NS |  | I-1 Cond. 2 | UL | 220000 | 76000 | 40000 | 66000 | 40000 | 216000 | 144000 | 72000 | 72000 | 42000 | 18000 | S1 | I-1 Cond. 2 | UL | 165000 | 57000 | 30000 | 49500 | 30000 | 162000 | 108000 | 54000 | 54000 | 31500 | 13500 | SM | I-1 Cond. 2 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 54000 | 36000 | 18000 | 18000 | 10500 | 4500 |  | I-1 Cond. 2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-2/I-2.1 | UL | UL | 15000 | 11000 | 12000 | NP W/ III-B or V-B Construction | 36000 | 24000 | 12000 | 12000 | 9500 | NP W/ III-B or V-B Construction | NS |  | I-2/I-2.1 | UL | UL | 60000 | 44000 | 48000 | NP W/ III-B or V-B Construction | 144000 | 96000 | 48000 | 48000 | 38000 | NP W/ III-B or V-B Construction | S1 | I-2/I-2.1 | UL | UL | 45000 | 33000 | 36000 | NP W/ III-B or V-B Construction | 108000 | 72000 | 36000 | 36000 | 28500 | NP W/ III-B or V-B Construction | SM (without ht. increase) | I-2/I-2.1 | UL | UL | 15000 | 11000 | 12000 | NP W/ III-B or V-B Construction | NP For CA. | NP For CA. | NP For CA. | 12000 | 9500 | NP W/ III-B or V-B Construction | SM (with ht. increase) | I-2/I-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ III-B or V-B | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-2/I-2.1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ III-B or V-B | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-3 | UL | UL | 15000 | 10000 | 10500 | 7500 | 36000 | 24000 | 12000 | 12000 | 7500 | 5000 | NS |  | I-3 | UL | UL | 60000 | 40000 | 42000 | 30000 | 144000 | 96000 | 48000 | 48000 | 30000 | 20000 | S1 | I-3 | UL | UL | 45000 | 30000 | 31500 | 22500 | 108000 | 72000 | 36000 | 36000 | 22500 | 15000 | SM (without ht. increase) | I-3 | UL | 30200 | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP For CA. | NP For CA. | NP For CA. | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | SM (with ht. increase) | I-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-4 | UL | 60500 | 26500 | 13000 | 23500 | 13000 | 76500 | 51000 | 25500 | 25500 | 18500 | 9000 | NS |  | I-4 | UL | 121000 | 106000 | 52000 | 94000 | 52000 | 306000 | 204000 | 102000 | 102000 | 74000 | 36000 | S1 | I-4 | UL | 181500 | 79500 | 39000 | 70500 | 39000 | 229500 | 153000 | 76500 | 76500 | 55500 | 27000 | SM (without ht. increase) | I-4 | UL | 60500 | 26500 | 13000 | 23500 | 13000 | 76500 | 51000 | 25500 | 25500 | 18500 | 9000 | SM (with ht. increase) | I-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
L | UL | 60000 | 37500 | 17500 | 28500 | 17500 | 6000 | 37500 | 36000 | 36000 | 18000 | 6500 | NS |  | L | UL | 60000 | 37500 | 17500 | 28500 | 17500 | 60000 | 37500 | 36000 | 36000 | 18000 | 6500 | S-1 | L | UL | 60000 | 37500 | 17500 | 28500 | 17500 | 60000 | 37500 | 36000 | 36000 | 18000 | 6500 | SM | L | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | L | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | L | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
M | UL | UL | 21500 | 12500 | 18500 | 12500 | 61500 | 41000 | 26625 | 20500 | 14000 | 9000 | NS |  | M | UL | UL | 86000 | 50000 | 74000 | 50000 | 246000 | 164000 | 102500 | 82000 | 56000 | 36000 | S-1 | M | UL | UL | 64500 | 37500 | 55500 | 37500 | 184500 | 123000 | 76875 | 61500 | 42000 | 27000 | SM | M | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | M | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | M | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 26625 | 20500 | 12000 | 7000 | NS |  | R-1 | UL | UL | 96000 | 64000 | 96000 | 64000 | 246000 | 164000 | 102500 | 82000 | 48000 | 28000 | S1 | R-1 | UL | UL | 72000 | 48000 | 72000 | 48000 | 184500 | 123000 | 76875 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | S13R
R-2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 26625 | 20500 | 12000 | 7000 | NS |  | R-2 | UL | UL | 96000 | 64000 | 96000 | 64000 | 246000 | 164000 | 102500 | 82000 | 48000 | 28000 | S1 | R-2 | UL | UL | 72000 | 48000 | 72000 | 48000 | 184500 | 123000 | 76875 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | S13R
R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 12000 | NP / Construction V-A Only | NS |  | R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 48000 | NP / Construction V-A Only | S1 | R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 36000 | NP / Construction V-A Only | SM (without ht. increase) | R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 36000 w/ Ht. Increase | NP / Construction V-A Only | SM (with ht. increase) | R-2 Type VA construction | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2 Type VA construction | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | S13R
R-2.1 | UL | 55000 | 19000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 16500 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 216000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 10500 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NS |  | R-2.1 | UL | 220000 | 76000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 66000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 216000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 42000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | S1 | R-2.1 | UL | 165000 | 57000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 49500 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 162000 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 31500 | NP W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | SM (without ht. increase) | R-2.1 | UL | 55000 | 19000 | W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 16500 | W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 54000 | W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | 10500 | W/ II-B, III-B, IV-A (216,000 Sprinkled), IV-B, IV-C, IV-HT, V-B Construction | SM (with ht. increase) | R-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2.1 | UL | 55000 | 19000 | NP | 16500 | NP | NP | NP | NP | NP | 16500 | NP | S13R
R-2.2 (CA Only) | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NS |  | R-2.2 (CA Only) | UL | UL | 96000 | NP W/ II-B & III-BConstruction | 9600 | NP W/ II-B & III-BConstruction | 246000 | 164000 | 102500 | 82000 | 48000 | 28000 | S1 | R-2.2 (CA Only) | UL | UL | 72000 | 48000 | 72000 | 48000 | 184500 | 123000 | 76875 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-2.2 (CA Only) | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-2.2 (CA Only) | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2.2 (CA Only) | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | NS |  | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | S1 | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | SM | R-3/R-3.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | SM (with ht. increase) | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | S13D | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | S13R
R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | NS |  | R-4 | UL | UL | 96000 | 64000 | 96000 | 64000 | 246000 | 164000 | 102500 | 82000 | 48000 | 28000 | S1 | R-4 | UL | UL | 72000 | 48000 | 7222 | 48000 | 184500 | 123000 | 76875 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 |  | R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 61500 | 41000 | 25625 | 20500 | 12000 | 7000 | S13R
S-1 | UL | 48000 | 26000 | 17500 | 26000 | 17500 | 76500 | 51000 | 31875 | 25500 | 14000 | 9000 | NS |  | S-1 | UL | 192000 | 104000 | 70000 | 104000 | 70000 | 306000 | 204000 | 127500 | 102000 | 56000 | 36000 | S1 | S-1 | UL | 144000 | 48000 | 52500 | 78000 | 52500 | 229500 | 153000 | 95625 | 76500 | 42000 | 27000 | SM | S-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
S-2 | UL | 79000 | 39000 | 26000 | 39000 | 26000 | 115500 | 77000 | 48125 | 38500 | 21000 | 13500 | NS |  | S-2 | UL | 316000 | 156000 | 104000 | 156000 | 104000 | 462000 | 308000 | 192500 | 154000 | 84000 | 54000 | S1 | S-2 | UL | 237000 | 117000 | 78000 | 117000 | 78000 | 346500 | 231000 | 144375 | 115500 | 63000 | 40500 | SM | S-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
U | UL | 35500 | 19000 | 8500 | 14000 | 8500 | 54000 | 36000 | 22500 | 18000 | 9000 | 5500 | NS |  | U | UL | 142000 | 76000 | 34000 | 56000 | 34000 | 216000 | 144000 | 90000 | 72000 | 36000 | 22000 | S1 | U | UL | 106500 | 57000 | 25500 | 42000 | 25500 | 162000 | 108000 | 67500 | 54000 | 27000 | 16500 | SM | U | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | U | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | U | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
9000 | [11 empty] | 9000 | 9500 |  | 36000 | [11 empty] | 36000 | 38000 | 27000 | [11 empty] | 27000 | 28500 | No Limitations | [13 empty] | NP W/ 13D | [11 empty] | NP W/ 13D | NP W/ 13D | NP W/13R | [11 empty] | NP W/13R | NP W/13R
area increase | [11 empty] | occ1 | occ2 |  | area increase | [11 empty] | occ1 | occ2 | area increase | [11 empty] | occ1 | occ2 | area increase | [13 empty] | area increase | [11 empty] | occ1 | occ2 | area increase | [11 empty] | occ1 | occ2
DO NOT OVERIDE BELOW |  |  |  | For Mixed Occ. #1 |  |  | For Mixed Occ. #2
B | V-B |  |  | DO NOT OVERIDE BELOW |  |  | DO NOT OVERIDE BELOW
|  |  |  | B | V-B |  | E
Note: UL = Unlimited; NP = Not Permitted;
For SI: 1 square foot = 0.0929 m2
NS | = Buildings not equipped throughout with an automatic sprinkler system.
S1 | = Buildings a maximum of one story above grade equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
SM | = Buildings two or more stories above grade equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
S13R | = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2.
S13D | = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.3.

## Allowable Bldg Ht Table 504.3 (hidden)
NOT SPRINKLED | [9 empty] | SPRINKLERS (S1 & SM) | [9 empty] | AREA INCREASE LIMITATIONS | [9 empty] | S13D SPRINKLERS | [9 empty] | S13R SPRINKLERS
| I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B
A-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-1 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | A-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-2 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | A-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-3 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-3 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-4 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | A-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-4 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-4 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
A-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-5 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | A-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | A-5 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | A-5 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
B | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | B | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | B | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | B | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | B | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
E | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | E | UL | 160 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | E | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | E | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | E | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
F-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | F-1 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | F-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | F-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | F-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
F-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | F-2 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | F-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | F-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | F-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-3 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-3 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-4 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | H-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-4 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-4 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
H-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-5 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | H-5 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | H-5 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-1 Cond. 1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-1 Cond. 1 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | I-1 Cond. 1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-1 Cond. 1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-1 Cond. 1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
I-1 Cond. 2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-1 Cond. 2 | UL | 180 | 85 | 55 | 65 | 55 | 65 | 50 | 40 | I-1 Cond. 2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-1 Cond. 2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-1 Cond. 2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-2/I-2.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-2/I-2.1 | UL | 180 | 85 | 55 | 65 | 55 | 65 | 50 | 40 | I-2/I-2.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-2/I-2.1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-2/I-2.1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-3 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | I-3 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-3 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-3 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
I-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | I-4 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | I-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 50 | I-4 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | I-4 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
L | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | L | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | L | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | L | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | L | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
M | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | M | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | M | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | M | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | M | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
R-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-1 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | R-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | R-1 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 50 | 40
R-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-2 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | R-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 60 | 40 | R-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | R-2 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 50 | 40
R-2.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-2.1 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | R-2.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | R-2.1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 40 | R-2.1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
R-2.2 (CA Only) | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | R-2.2 (CA Only) | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | R-2.2 (CA Only) | UL | 160 | 65 | 55 | 65 | 55 | 65 | 60 | 40 | R-2.2 (CA Only) | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | R-2.2 (CA Only) | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
R-3/R-3.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-3/R-3.1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-3/R-3.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | R-3/R-3.1 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 50 | 40 | R-3/R-3.1 | 60 | 60 | 60 | 55 | 60 | 55 | 60 | 50 | 40
R-4 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | R-4 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | R-4 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | R-4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 40 | R-4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
S-1 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | S-1 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | S-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | S-1 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | S-1 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
S-2 | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | S-2 | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | S-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | S-2 | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | S-2 | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
U | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 | U | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 | U | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | U | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | NP W/13D | U | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R | NP W/ 13R
40 | [9 empty] | 60 | [9 empty] | No Limitations | [9 empty] | NP W/13D | [9 empty] | NP W/ 13R
DO NOT OVERIDE BELOW
B | V-B
Note: UL = Unlimited; NP = Not Permitted;
For SI: 1 square foot = 304.8 mm
NS = Buildings not equipped throughout with an automatic sprinkler system.
S = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
S13R = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2
S13D = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.3.

## Allowable Stories Table 504.4 (hidden)
NOT SPRINKLED | [10 empty] | SPRINKLED (S1 & SM) | [10 empty] | AREA INCREASE LIMITATIONS | [10 empty] | SPRINKLED 13D | [10 empty] | SPRINKLED 13R
| I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B
A-1 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | NS | A-1 | UL | 6 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | S (without area increase) | A-1 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | S (with area increase) | A-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-2 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | NS | A-2 | UL | 12 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | S (without area increase) | A-2 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | S (with area increase) | A-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-3 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | NS | A-3 | UL | 12 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | S (without area increase) | A-3 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | S (with area increase) | A-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-4 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | NS | A-4 | UL | 12 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | S (without area increase) | A-4 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1 | S (with area increase) | A-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | NS | A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | S | A-5 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
B | UL | 11 | 5 | 3 | 5 | 3 | 5 | 3 | 2 | NS | B | UL | 12 | 6 | 4 | 6 | 4 | 6 | 4 | 3 | S | B | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | B | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | B | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
E | UL | 5 | 3 | 2 | 3 | 2 | 3 | 1 | 1 | NS | E | UL | 6 | 4 | 3 | 4 | 3 | 4 | 2 | 2 | S (without area increase) | E | UL | 5 | 3 | 2 | 3 | 2 | 3 | 1 | 1 | S (with area increase) | E | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | E | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-1 | UL | 11 | 4 | 2 | 3 | 2 | 4 | 2 | 1 | NS | F-1 | UL | 12 | 5 | 3 | 4 | 3 | 5 | 3 | 2 | S | F-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-2 | UL | 11 | 5 | 3 | 4 | 3 | 5 | 3 | 2 | NS | F-2 | UL | 12 | 6 | 4 | 5 | 4 | 6 | 4 | 3 | S | F-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | NP W/ V-B Construction | NS | H-1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | NP W/ V-B Construction | S | H-1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | NP W/ V-B Construction |  | H-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ V-B Construction |  | H-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ V-B Construction
H-2 | 20 | 3 | 2 | 1 | 2 | 1 | 2 | 1 | NP W/ V-B Construction | NS | H-2 | 20 | 3 | 2 | 1 | 2 | 1 | 2 | 1 | 1 | S | H-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-3 | 20 | 6 | 4 | 2 | 4 | 2 | 4 | 2 | 1 | NS | H-3 | 20 | 6 | 4 | 2 | 4 | 2 | 4 | 2 | 1 | S | H-3 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-4 | 20 | 7 | 5 | 3 | 5 | 3 | 5 | 3 | 2 | NS | H-4 | 20 | 8 | 6 | 4 | 6 | 4 | 6 | 4 | 3 | S (without area increase) | H-4 | 20 | 7 | 5 | 3 | 5 | 3 | 5 | 3 | 2 | S (with area increase) | H-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-5 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | NS | H-5 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | S | H-5 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-1 Cond. 1 | UL | 9 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | NS | I-1 Cond. 1 | UL | 10 | 5 | 4 | 5 | 4 | 5 | 4 | 3 | S | I-1 Cond. 1 | NP | NP | NP | NP | NP | NP | NP | NP | NP | NS | I-1 Cond. 1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 1 | UL | 9 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | S13R
I-1 Cond. 2 | UL | 9 | 4 | 3 | 4 | 3 | 4 | 3 | 2 | NS | I-1 Cond. 2 | UL | 10 | 5 | 3 | 4 | 3 | 4 | 3 | 2 | S | I-1 Cond. 2 | NP | NP | NP | NP | NP | NP | NP | NP | NP | NS | I-1 Cond. 2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-2/I-2.1 | UL | 4 | 2 | 1 | 1 | NP W/ III-B or V-B Construction | 1 | 1 | NP W/ III-B or V-B Construction | NS | I-2/I-2.1 | UL | 5 | 3 | 1 | 1 | NP W/ III-B or V-B Construction | 1 | 1 | NP W/ III-B or V-B Construction | S (without area increase) | I-2/I-2.1 | UL | 4 | 2 | 1 | 1 | NP W/ III-B or V-B Construction | 1 | 1 | NP W/ III-B or V-B Construction | S (with area increase) | I-2/I-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ III-B or V-B | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-2/I-2.1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ III-B or V-B | NP W/13R | NP W/13R | NP W/13R
I-3 | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NS | I-3 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 3 | 2 | S (without area increase) | I-3 | UL | 2 | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | S (with area increase) | I-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-4 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 1 | 1 | NS | I-4 | UL | 6 | 4 | 3 | 4 | 3 | 4 | 2 | 2 | S (without area increase) | I-4 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 1 | 1 | S (with area increase) | I-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
L | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NS | L | 20 | 6 | 5 | 3 | 5 | 3 | 5 | 3 | 2 | S | L | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | L | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | L | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
M | UL | 11 | 4 | 2 | 4 | 2 | 4 | 3 | 1 | NS | M | UL | 12 | 5 | 3 | 5 | 3 | 5 | 4 | 2 | S | M | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | M | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | M | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | NS | R-1 | UL | 12 | 5 | 5 | 5 | 5 | 5 | 4 | 3 | S (without area increase) | R-1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | S (with area increase) | R-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | S13R
R-2 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | NS | R-2 | UL | 12 | 5 | 5 | 5 | 5 | 5 | 4 | 3 | S (without area increase) | R-2 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | S (with area increase) | R-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | S13R
R-2.2 (CA Only) | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NP W/O S1 or SM Spinklers | NS | R-2.2 (CA Only) | UL | 12 | 5 | 5 | 5 | 5 | 5 | 4 | 3 | S (without area increase) | R-2.2 (CA Only) | UL | 11 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | S (with area increase) | R-2.2 (CA Only) | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2.2 (CA Only) | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-2.1 | UL | 6 | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | NS | R-2.1 | UL | 6 | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | S | R-2.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | R-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ 13D | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ 13D | NP W/ II-B, III-B, IV-HT, V-B Construction |  | R-2.1 | UL | 4 | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | NP W/ II-B, III-B, IV-HT, V-B Construction | 3 | NP W/ II-B, III-B, IV-HT, V-B Construction | S13R
R-3/R-3.1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | NS | R-3/R-3.1 | UL | 12 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | S | R-3/R-3.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | R-3/R-3.1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | S13D | R-3/R-3.1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | S13R
R-4 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | NS | R-4 | UL | 11 | 5 | 5 | 5 | 5 | 5 | 4 | 3 | S | R-4 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | R-4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | S13D | R-4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | S13R
S-1 | UL | 11 | 4 | 2 | 3 | 2 | 4 | 3 | 1 | NS | S-1 | UL | 12 | 5 | 3 | 4 | 3 | 5 | 4 | 2 | S | S-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
S-2 | UL | 11 | 5 | 3 | 4 | 3 | 4 | 4 | 2 | NS | S-2 | UL | 12 | 6 | 4 | 5 | 4 | 5 | 5 | 3 | S | S-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
U | UL | 5 | 4 | 2 | 3 | 2 | 4 | 2 | 1 | NS | U | UL | 6 | 5 | 3 | 4 | 3 | 5 | 3 | 2 | S | U | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | U | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | U | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
2 | [10 empty] | 3 | [10 empty] | No Limitations | [10 empty] | NP W/ 13D | [10 empty] | NP W/13R
DO NOT OVERIDE BELOW
B | V-B
Note: UL = Unlimited; NP = Not Permitted;
NS = Buildings not equipped throughout with an automatic sprinkler system.
S = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
S13R = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2
S13D = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.3.

## Allowable area Table 506.2 (hidden)
NOT SPRINKLED | [11 empty] | SPRINKLED (S1) | [10 empty] | SPRINKLED MULTI-STORY (SM) | [10 empty] | AREA INCREASE LIMITATIONS | [10 empty] | SPRINKLED 13D | [10 empty] | SPRINKLED 13R
| I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  |  |  | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B |  | 0 | I-A | I-B | II-A | II-B | III-A | III-B | IV-HT | V-A | V-B
A-1 | UL | UL | 15500 | 8500 | 14000 | 8500 | 15000 | 11500 | 5500 | NS |  | A-1 | UL | UL | 62000 | 34000 | 56000 | 34000 | 60000 | 46000 | 22000 | S1 | A-1 | UL | UL | 46500 | 25500 | 42000 | 25500 | 45000 | 34500 | 16500 | SM | A-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-2 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000 | NS |  | A-2 | UL | UL | 62000 | 38000 | 56000 | 38000 | 60000 | 46000 | 24000 | S1 | A-2 | UL | UL | 46500 | 28500 | 42000 | 28500 | 45000 | 34500 | 18000 | SM (without ht. increase) | A-2 | UL | UL | 15500 | 9500 | 14000 | 95000 | 15000 | 11500 | 6000 | SM (with ht. increase) | A-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-3 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000 | NS | 0 | A-3 | UL | UL | 62000 | 38000 | 56000 | 38000 | 60000 | 46000 | 24000 | S1 | A-3 | UL | UL | 46500 | 28500 | 42000 | 28500 | 45000 | 34500 | 18000 | SM | A-3 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-4 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000 | NS |  | A-4 | UL | UL | 62000 | 38000 | 56000 | 38000 | 60000 | 46000 | 24000 | S1 | A-4 | UL | UL | 46500 | 28500 | 42000 | 28500 | 45000 | 34500 | 18000 | SM (without ht. increase) | A-4 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000 | SM (with ht. increase) | A-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | NS |  | A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | S1 | A-5 | UL | UL | UL | UL | UL | UL | UL | UL | UL | SM | A-5 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | A-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | A-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
B | UL | UL | 37500 | 23000 | 28500 | 19000 | 36000 | 18000 | 9000 | NS |  | B | UL | UL | 150000 | 92000 | 114000 | 76000 | 144000 | 72000 | 36000 | S1 | B | UL | UL | 112500 | 69000 | 85500 | 57000 | 108000 | 54000 | 27000 | SM | B | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | B | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | B | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
E | UL | UL | 26500 | 14500 | 23500 | 14500 | 25500 | 18500 | 9500 | NS |  | E | UL | UL | 106000 | 58000 | 94000 | 58000 | 102000 | 74000 | 38000 | S1 | E | UL | UL | 79500 | 43500 | 70500 | 43500 | 76500 | 55500 | 28500 | SM (without ht. increase) | E | UL | UL | 26500 | 14500 | 23500 | 14500 | 25500 | 18500 | 9500 | SM (with ht. increase) | E | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | E | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-1 | UL | UL | 25000 | 15500 | 19000 | 12000 | 33500 | 1400 | 8500 | NS |  | F-1 | UL | UL | 100000 | 62000 | 76000 | 48000 | 134000 | 56000 | 34000 | S1 | F-1 | UL | UL | 75000 | 46500 | 57000 | 36000 | 100500 | 42000 | 25500 | SM | F-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
F-2 | UL | UL | 37500 | 23000 | 28500 | 18000 | 50500 | 21000 | 13000 | NS |  | F-2 | UL | UL | 150000 | 92000 | 114000 | 72000 | 202000 | 84000 | 52000 | S1 | F-2 | UL | UL | 112500 | 69000 | 85500 | 54000 | 151500 | 63000 | 39000 | SM | F-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | F-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | F-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-1 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 7500 | NP W/ V-B Construction | NS |  | H-1 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 7500 | NP W/ V-B Construction | S1 | H-1 | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP 1-Story Only | NP | H-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ V-B Construction |  | H-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ V-B Construction
H-2 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 7500 | 3000 | NS |  | H-2 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 7500 | 3000 | S1 | H-2 | 21000 | 16500 | 11000 | 70000 | 9500 | 7000 | 10500 | 7500 | 3000 | SM | H-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-3 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25500 | 10000 | 5000 | NS |  | H-3 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25500 | 10000 | 5000 | S1 | H-3 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25500 | 10000 | 5000 | SM | H-3 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | H-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-4 | UL | UL | 37500 | 17500 | 28500 | 17500 | 36000 | 18000 | 6500 | NS |  | H-4 | UL | UL | 150000 | 70000 | 114000 | 70000 | 144000 | 72000 | 26000 | S1 | H-4 | UL | UL | 112500 | 52500 | 85500 | 52500 | 108000 | 54000 | 19500 | SM (without ht. increase) | H-4 | UL | UL | 37500 | 17500 | 28500 | 17500 | 36000 | 18000 | 6500 | SM (with ht. increase) | H-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
H-5 | UL | UL | 37500 | 23000 | 28500 | 19000 | 36000 | 18000 | 9000 | NS |  | H-5 | UL | UL | 150000 | 92000 | 114000 | 76000 | 144000 | 72000 | 36000 | S1 | H-5 | UL | UL | 112500 | 69000 | 85500 | 57000 | 10800 | 54000 | 27000 | SM (without ht. increase) | H-5 | UL | UL | 37500 | 23000 | 28500 | 19000 | 36000 | 18000 | 9000 | SM (with ht. increase) | H-5 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | H-5 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-1 Cond. 1 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 18000 | 10500 | 4500 | NS |  | I-1 Cond. 1 | UL | 220000 | 76000 | 40000 | 66000 | 40000 | 72000 | 42000 | 18000 | S1 | I-1 Cond. 1 | UL | 165000 | 57000 | 30000 | 49500 | 30000 | 54000 | 31500 | 13500 | SM | I-1 Cond. 1 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 18000 | 10500 | 4500 |  | I-1 Cond. 1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 1 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 18000 | 10500 | 4500 | S13R
I-1 Cond. 2 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 18000 | 10500 | 4500 | NS |  | I-1 Cond. 2 | UL | 220000 | 76000 | 40000 | 66000 | 40000 | 72000 | 42000 | 18000 | S1 | I-1 Cond. 2 | UL | 165000 | 57000 | 30000 | 49500 | 30000 | 54000 | 31500 | 13500 | SM | I-1 Cond. 2 | UL | 55000 | 19000 | 10000 | 16500 | 10000 | 18000 | 10500 | 4500 |  | I-1 Cond. 2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-1 Cond. 2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-2/I-2.1 | UL | UL | 15000 | 11000 | 12000 | NP W/ III-B or V-B Construction | 12000 | 9500 | NP W/ III-B or V-B Construction | NS |  | I-2/I-2.1 | UL | UL | 60000 | 44000 | 48000 | NP W/ III-B or V-B Construction | 48000 | 38000 | NP W/ III-B or V-B Construction | S1 | I-2/I-2.1 | UL | UL | 45000 | 33000 | 36000 | NP W/ III-B or V-B Construction | 36000 | 28500 | NP W/ III-B or V-B Construction | SM (without ht. increase) | I-2/I-2.1 | UL | UL | 15000 | 11000 | 12000 | NP W/ III-B or V-B Construction | 12000 | 9500 | NP W/ III-B or V-B Construction | SM (with ht. increase) | I-2/I-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ III-B or V-B | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-2/I-2.1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/ III-B or V-B | NP W/13R | NP W/13R | NP W/13R
I-3 | UL | UL | 15000 | 10000 | 10500 | 7500 | 12000 | 7500 | 5000 | NS |  | I-3 | UL | UL | 45000 | 40000 | 42000 | 30000 | 48000 | 30000 | 20000 | S1 | I-3 | UL | UL | 45000 | 30000 | 31500 | 22500 | 36000 | 22500 | 15000 | SM (without ht. increase) | I-3 | UL | 15100 | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | NP / Use I-A or I-B Construction | SM (with ht. increase) | I-3 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-3 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
I-4 | UL | 60500 | 26500 | 13000 | 23500 | 13000 | 25500 | 18500 | 9000 | NS |  | I-4 | UL | 121000 | 106000 | 52000 | 94000 | 52000 | 102000 | 74000 | 36000 | S1 | I-4 | UL | 181500 | 79500 | 39000 | 70500 | 39000 | 76500 | 55500 | 27000 | SM (without ht. increase) | I-4 | UL | 60500 | 26500 | 13000 | 23500 | 13000 | 25500 | 18500 | 9000 | SM (with ht. increase) | I-4 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | I-4 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
L | UL | 60000 | 37500 | 17500 | 28500 | 17500 | 36000 | 18000 | 6500 | NS |  | L | UL | 60000 | 37500 | 17500 | 28500 | 17500 | 36000 | 18000 | 6500 | S-1 | L | UL | 60000 | 37500 | 17500 | 28500 | 17500 | 36000 | 18000 | 6500 | SM | L | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | L | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | L | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
M | UL | UL | 21500 | 12500 | 18500 | 12500 | 20500 | 14000 | 9000 | NS |  | M | UL | UL | 86000 | 50000 | 74000 | 50000 | 82000 | 56000 | 36000 | S-1 | M | UL | UL | 64500 | 37500 | 55500 | 37500 | 61500 | 42000 | 27000 | SM | M | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | M | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | M | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | NS |  | R-1 | UL | UL | 96000 | 64000 | 96000 | 64000 | 82000 | 48000 | 28000 | S1 | R-1 | UL | UL | 72000 | 48000 | 72000 | 48000 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | S13R
R-2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | NS |  | R-2 | UL | UL | 96000 | 64000 | 96000 | 64000 | 82000 | 48000 | 28000 | S1 | R-2 | UL | UL | 72000 | 48000 | 72000 | 48000 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | S13R
R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 12000 | NP / Construction V-A Only | NS |  | R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 48000 | NP / Construction V-A Only | S1 | R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 36000 | NP / Construction V-A Only | SM (without ht. increase) | R-2 Type VA construction | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | NP / Construction V-A Only | 36000 w/ Ht. Increase | NP / Construction V-A Only | SM (with ht. increase) | R-2 Type VA construction | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2 Type VA construction | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | S13R
R-2.1 | UL | 55000 | 19000 | NP W/ II-B, III-B, IV-HT (OK Sprinkled), V-B Construction | 16500 | NP W/ II-B, III-B, IV-HT (OK Sprinkled), V-B Construction | NP W/ II-B, III-B, IV-HT (OK Sprinkled), V-B Construction | 16500 | NP W/ II-B, III-B, IV-HT (OK Sprinkled), V-B Construction | NS |  | R-2.1 | UL | 220000 | 76000 | 40000 | 66000 | 40000 | 72000 | 42000 | NP W/ V-B Construction | S1 | R-2.1 | UL | 165000 | 57000 | 30000 | 49500 | 30000 | 54000 | 31500 | NP W/ V-B Construction | SM (without ht. increase) | R-2.1 | UL | 55000 | 19000 | NP W II-B Construction | 16500 | NP W/ III-B Construction | NP W/ IV-HT Construction | 16500 | NP W/ V-B Construction | SM (with ht. increase) | R-2.1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2.1 | UL | 55000 | 19000 | NP | 16500 | NP | NP | 16500 | NP | S13R
R-2.2 (CA Only) | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NP W/O S1 or SM Sprinklers | NS |  | R-2.2 (CA Only) | UL | UL | 96000 | 64000 | 9600 | 64000 | 82000 | 48000 | 28000 | S1 | R-2.2 (CA Only) | UL | UL | 72000 | 48000 | 72000 | 48000 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-2.2 (CA Only) | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-2.2 (CA Only) | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | R-2.2 (CA Only) | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | NS |  | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | S1 | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | SM | R-3/R-3.1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | SM (with ht. increase) | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | S13D | R-3/R-3.1 | UL | UL | UL | UL | UL | UL | UL | UL | UL | S13R
R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | NS |  | R-4 | UL | UL | 96000 | 64000 | 96000 | 64000 | 82000 | 48000 | 28000 | S1 | R-4 | UL | UL | 72000 | 48000 | 7222 | 48000 | 61500 | 36000 | 21000 | SM (without ht. increase) | R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | SM (with ht. increase) | R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 |  | R-4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000 | S13R
S-1 | UL | 48000 | 26000 | 17500 | 26000 | 17500 | 25500 | 14000 | 9000 | NS |  | S-1 | UL | 192000 | 104000 | 70000 | 104000 | 70000 | 102000 | 56000 | 36000 | S1 | S-1 | UL | 144000 | 48000 | 52500 | 78000 | 52500 | 76500 | 42000 | 27000 | SM | S-1 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-1 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-1 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
S-2 | UL | 79000 | 39000 | 26000 | 39000 | 26000 | 38500 | 21000 | 13500 | NS |  | S-2 | UL | 316000 | 156000 | 104000 | 156000 | 104000 | 154000 | 84000 | 54000 | S1 | S-2 | UL | 237000 | 117000 | 78000 | 117000 | 78000 | 115500 | 63000 | 40500 | SM | S-2 | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | S-2 | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | S-2 | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
U | UL | 35500 | 19000 | 8500 | 14000 | 8500 | 18000 | 9000 | 5500 | NS |  | U | UL | 142000 | 76000 | 34000 | 56000 | 34000 | 72000 | 36000 | 22000 | S1 | U | UL | 106500 | 57000 | 25500 | 42000 | 25500 | 54000 | 27000 | 16500 | SM | U | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations | No Limitations |  | U | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D | NP W/ 13D |  | U | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R | NP W/13R
9000 | [8 empty] | 9000 | 9500 |  | 36000 | [8 empty] | 36000 | 38000 | 27000 | [8 empty] | 27000 | 28500 | No Limitations | [10 empty] | NP W/ 13D | [8 empty] | NP W/ 13D | NP W/ 13D | NP W/13R | [8 empty] | NP W/13R | NP W/13R
area increase | [8 empty] | occ1 | occ2 |  | area increase | [8 empty] | occ1 | occ2 | area increase | [8 empty] | occ1 | occ2 | area increase | [10 empty] | area increase | [8 empty] | occ1 | occ2 | area increase | [8 empty] | occ1 | occ2
DO NOT OVERIDE BELOW |  |  |  | For Mixed Occ. #1 |  |  | For Mixed Occ. #2
B | V-B |  |  | DO NOT OVERIDE BELOW |  |  | DO NOT OVERIDE BELOW
|  |  |  | B | V-B |  | E
Note: UL = Unlimited; NP = Not Permitted;
For SI: 1 square foot = 0.0929 m2
NS | = Buildings not equipped throughout with an automatic sprinkler system.
S1 | = Buildings a maximum of one story above grade equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
SM | = Buildings two or more stories above grade equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
S13R | = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2.
S13D | = Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.3.