## 2022 CEC - Commercial
Section 140.10: Photovoltaic & Battery Storage Systems
Occupancy Type: |  | Office | [5 empty] | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area)
[7 empty] | Climate Zone | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Photovoltiac Direct Current Size (KWPVdc=(CFAxA)/1000) |  |  |  |  | # of Panel Required (Based on average 320 Watts per Panel) | Sqauare Footage Needed (Based on 3'x5' Panel) | Grocery | 2.62 | 2.91 | 2.62 | 2.91 | 2.62 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 3.53 | 2.62
Sq. Ft.: | Climate Zone: | A: | Total PV Required in KW (KWPVdc): |  |  |  | High-Rise Multi-Family | 1.82 | 2.21 | 1.82 | 2.21 | 1.82 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.77 | 1.82
2400 | 9 | 3.13 | 7.512 |  | 23.475 | 352.125 | Office | 2.59 | 3.13 | 2.59 | 3.13 | 2.59 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.8 | 2.59
[7 empty] | Financial Institutions | 2.59 | 3.13 | 2.59 | 3.13 | 2.59 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.8 | 2.59
Battery Storage Rated Energy Capacity (KWhbatt=KWPVdcxB/D.05) | [6 empty] | Unleased Tenant Space | 2.59 | 3.13 | 2.59 | 3.13 | 2.59 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.8 | 2.59
KWPVdc: | B (Wh/W): | D: | Total Energy Capcity (Kwhbatt): |  |  |  | Retail | 2.62 | 2.91 | 2.62 | 2.91 | 2.62 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 2.91 | 3.53 | 2.62
7.512 | 1.68 | 80 | 14.1098 |  |  |  | School | 1.27 | 1.63 | 1.27 | 1.63 | 1.27 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 2.46 | 1.27
[7 empty] | Warehouse | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
Battery Storage Rated Power Capacity (KWbatt=KWPVdcxC) | [6 empty] | Auditorium | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
KWPVdc: | C (W/W): | Total Power Capacity in KW (Kwbatt): |  |  |  |  | Convention Center | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
7.512 | 0.42 | 3.155 |  |  |  |  | Hotel/Motel | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
[7 empty] | Library | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
Solar Access Roof Area (SARA): |  |  | 1400 | <---Area avaiable to install solar panels (See Joint Appendix JA11) |  |  | Medical Office Building/Clinic | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
[7 empty] | Restaurant | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
[7 empty] | Theater | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39
Section 110.10(b)1B: Minimum Solar Zone Area (Nonresidential)
Min. Solar Zone Area: |  |  | 360 | SQ. FT. |  |  | Battery Storage Capacity Factors
Note: | 1. Above value is based on sq. ft. inputed in Cell A6 | [6 empty] | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: Factor B; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: Factor C
| 2. Substract sq. ft. of skylight(s) from overall roof area. This will decrease the min. Solar Zone required. | [5 empty] | Grocery | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.03; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.26
[7 empty] | High-Rise Multi-Family | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.03; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.26
| 3. Section 110.10(b): Buildings up to 10,000 sq. ft. or less, Solar Zone(s) can be no less than 80 sq. ft. each. Buildings over 10,000 sq. ft., Solar Zone(s) can be no less than 160 sq. ft. each. Each zone(s) shall be no less than 5'x5' regardless of the square footage requirement. | [5 empty] | Office | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.68; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.42
[7 empty] | Financial Institutions | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.68; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.42
[7 empty] | Unleased Tenant Space | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.68; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.42
[7 empty] | Retail | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.03; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.26
[7 empty] | School | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 1.87; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.46
[7 empty] | Warehouse | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
[7 empty] | Auditorium | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
Note: | 1. See Joint Appendix JA12 for minimum battery efficiency (value in Cell D10) | [5 empty] | Convention Center | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
[7 empty] | Hotel/Motel | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
[7 empty] | Library | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
[7 empty] | Medical Office Building/Clinic | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
[7 empty] | Restaurant | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23
[7 empty] | Theater | Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 1: 0.93; Factor A - Minimum PV Capacity (W/ft2 of Conditioned Floor Area) 2: 0.23

## 2022 CEC - Residential
Section 150.1(14): Photovoltaic Requirements
Table 150.1-C-CFA AND DWELLING UNIT ADJUSTMENT FACTORS
[8 empty] | Climate Zone | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Annual Photovoltaic Electrical Output (kWpv=(CFAxA)/1000+(NDUxB) | [5 empty] | # of Panel Required (Based on average 320 Watts per Panel) | Sqauare Footage Needed (Based on 3'x5' Panel) | A-CFA | 0.793 | 0.621 | 0.628 | 0.586 | 0.585 | 0.594 | 0.572 | 0.586 | 0.613 | 0.627 | 0.836 | 0.613 | 0.894 | 0.741 | 1.56 | 0.59
Conditioned Floor Area (CFA) | Climate Zone: | A: | # of Dwelling Units (NDU): | B: | Total PV Required in kW (kWPV): |  |  | B-Dwelling Units | 1.27 | 1.22 | 1.12 | 1.21 | 1.06 | 1.23 | 1.15 | 1.37 | 1.36 | 1.41 | 1.44 | 1.4 | 1.51 | 1.26 | 1.47 | 1.22
1410 | 13 | 0.894 | 1 | 1.51 | 2.7705 | 8.6579 | 129.8691
Solar Acces Roof Area (SARA)
310 | <--Sq. Ft. of available Solar area on roof
Is Battery Storage System Provided?
No

## 2025 CEC - Commercial
Section 140.10: Photovoltaic & Battery Storage Systems
Occupancy Type: |  | Office, Financial Institution, Unleased Tenant Space, Medical Office Building/Clinic | [8 empty] | Table 140.10-A-PV Capacity Factors (W/ft2 of Conditioned Floor Area) | [16 empty] | Table 140.10-B-BESS Capacity Factors (Wh/ft2 of Conditioned Floor Area)
[10 empty] | Climate Zone | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | Climate Zone | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Photovoltiac Direct Current Size (kWPVdc=(CFAxA)/1000) | [5 empty] | # of Panel Required (Based on average 320 Watts per Panel) |  | Sqauare Footage Needed (Based on 3'x5' Panel) |  | Events & Exhibits | 3.48 | 4.28 | 3.66 | 4.32 | 3.77 | 4.05 | 4.28 | 4.83 | 4.63 | 4.8 | 5.04 | 4.44 | 4.95 | 4.36 | 5.48 | 3.38 | Events & Exhibits | 1.82 | 1.95 | 1.74 | 2.12 | 1.91 | 2.13 | 2.24 | 2.3 | 2.36 | 2.47 | 2.62 | 2.16 | 2.64 | 2.68 | 3.22 | 1.89
Conditioned Floor Area (CFA) | Climate Zone: | A: | Total PV Required in KW (kWPVdc): | [6 empty] | Library | 0.39 | 3.23 | 2.59 | 3.25 | 2.48 | 2.74 | 3.04 | 3.49 | 3.32 | 3.69 | 3.79 | 3.32 | 3.79 | 3.37 | 4.49 | 2.84 | Library | 0.37 | 7.17 | 5.97 | 6.75 | 5.64 | 6.08 | 6.19 | 7.13 | 7.18 | 7.56 | 7.17 | 6.93 | 6.88 | 6.81 | 7.93 | 6.4
3600 | 9 | 3.13 | 11.268 |  |  | 35.2125 |  | 528.1875 |  | Hotel/Motel | 1.63 | 1.9 | 1.66 | 1.97 | 1.69 | 1.87 | 1.94 | 2.22 | 2.09 | 2.2 | 2.3 | 2.05 | 2.3 | 2.02 | 2.72 | 1.73 | Hotel/Motel | 0.86 | 0.84 | 0.77 | 0.92 | 0.81 | 0.89 | 0.9 | 1.01 | 1 | 1.11 | 1.14 | 0.96 | 1.18 | 1.18 | 1.49 | 0.85
[10 empty] | Office, Financial Institution, Unleased Tenant Space, Medical Office Building/Clinic | 2.59 | 3.13 | 2.59 | 3.13 | 2.59 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.8 | 2.59 | Office, Financial Institution, Unleased Tenant Space, Medical Office Building/Clinic | 0 | 5.26 | 4.35 | 5.26 | 4.35 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 5.26 | 6.39 | 4.35
Battery Energy Storage System Rated Usable Energy Capacity (kWhbatt=[CFA x B)/(1000 x C0.5)] | [9 empty] | Restaurants | 8.55 | 9.32 | 8.16 | 9.65 | 8.21 | 8.73 | 9.11 | 10.18 | 9.75 | 10.28 | 10.85 | 9.73 | 10.69 | 9.73 | 12.25 | 8.47 | Restaurants | 4.36 | 4.11 | 3.78 | 4.37 | 3.89 | 4.02 | 4.11 | 4.49 | 4.47 | 4.82 | 5.05 | 4.43 | 5.05 | 5.24 | 6.23 | 4.11
Conditioned Floor Area (CFA) | B (Wh/ft2): | C: | Total Energy Capcity (kWhbatt): |  |  | Rating of AC to DC Efficiency: | 90% |  |  | Retail, Grocery | 3.14 | 3.49 | 3.01 | 3.61 | 3.05 | 3.27 | 3.45 | 3.83 | 3.65 | 3.81 | 4.09 | 3.64 | 3.99 | 3.71 | 4.6 | 3.21 | Retail, Grocery | 1.89 | 1.82 | 2.7 | 1.82 | 1.72 | 1.8 | 1.76 | 1.92 | 1.97 | 2.05 | 2.22 | 1.95 | 2.16 | 2.29 | 2.66 | 1.91
3600 | 5.26 | 90% | 19.9603 | [6 empty] | School | 1.27 | 1.63 | 1.27 | 1.63 | 1.27 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 2.46 | 1.27 | School | 0 | 3.05 | 2.38 | 3.05 | 2.38 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 4.6 | 2.38
[10 empty] | Warehouse | 0.39 | 0.44 | 0.39 | 0.44 | 0.39 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.58 | 0.39 | Warehouse | 0.37 | 0.41 | 0.37 | 0.41 | 0.37 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.54 | 0.37
Battery Energy Storage System Rated Usable Energy Capacity, SARA-Adjusted (kWhbatt=[CFA x B)/(1000 x C0.5)] x (kWpvdc,SARA / kWpvdc) | [8 empty] | Factor for Slope | Religious Worship | 4.25 | 4.65 | 3.49 | 4.52 | 3.72 | 4.29 | 4.64 | 5.89 | 5.3 | 5.67 | 5.89 | 4.99 | 5.78 | 4.63 | 7.57 | 3.9 | Religious Worship | 2.21 | 2.25 | 1.74 | 2.42 | 2.08 | 2.75 | 2.94 | 3.37 | 3.17 | 3.37 | 3.58 | 2.72 | 3.62 | 3.21 | 4.89 | 2.37
Conditioned Floor Area (CFA) | B (Wh/ft2): | C: | Total Energy Capcity (kWhbatt): |  |  | Roof Slope in Inches: | 0.25 | : 12 | 14 | Sports & Recreation | 2.47 | 1.97 | 1.54 | 2.03 | 1.6 | 1.84 | 1.98 | 2.63 | 2.47 | 2.6 | 2.75 | 2.2 | 2.72 | 2.15 | 4.03 | 1.81 | Sports & Recreation | 1.26 | 0.98 | 0.76 | 1.14 | 0.86 | 1.2 | 1.23 | 1.57 | 1.53 | 1.65 | 1.83 | 1.27 | 1.86 | 1.57 | 3.02 | 1.13
3600 | 5.26 | 90% | 13.3919 |  |  | Note: 140.10(a), Exception 5: Multitenant building tenant spaces less than 2,000 sq. ft. do not require PV system. |  |  |  | Multifamily > 3 Stories | 1.82 | 2.21 | 1.82 | 2.21 | 1.82 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.77 | 1.82 | Multifamily > 3 Stories | 1.88 | 2.27 | 1.88 | 2.27 | 1.88 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.85 | 1.88
BESS Minimum Rated Power Capacity (kWbatt=kWbatt/4) | [5 empty] | BESS = Battery Energy Storage System |  |  |  |  | Table 140.10-A-PV Capacity Factors (W/ft2 of Conditioned Floor Area) 1: 77.14%; Table 140.10-A-PV Capacity Factors (W/ft2 of Conditioned Floor Area) 2: <- Percentage difference between Cells D6 & D10
kWbatt: |  | Total Power Capacity in KW (kWbatt): | [8 empty] | Table 140.10-A-PV Capacity Factors (W/ft2 of Conditioned Floor Area) 1: 18.85%; Table 140.10-A-PV Capacity Factors (W/ft2 of Conditioned Floor Area) 2: <- Percentage difference between Cells D6 & D14
13.3919 |  | 3.348
Solar Access Roof Area (SARA): |  |  | 540 | 15% | <---Percentage of area avaiable to install solar panels or enter sq. ft. that is available in Cell D20 (See Joint Appendix JA11)
Section 110.10(b)1B: Minimum Solar Zone Area (Nonresidential)
Min. Solar Zone Area: |  |  | 540 | SQ. FT.
Note: | 1. Substract sq. ft. of skylight(s) from overall roof area. This will decrease the min. Solar Zone required.
2. Section 110.10(b): Buildings up to 10,000 sq. ft. or less, Solar Zone(s) can be no less than 80 sq. ft. each. Buildings over 10,000 sq. ft., Solar Zone(s) can be no less than 160 sq. ft. each. Each zone(s) shall be no less than 5'x5' regardless of the square footage requirement.

## 2025 CEC - Residential (2)
Section 150.1(14): Photovoltaic Requirements
Table 150.1-C-CFA AND DWELLING UNIT ADJUSTMENT FACTORS
[10 empty] | Climate Zone | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Annual Photovoltaic Electrical Output (kWpv=(CFAxA)/1000+(NDUxB) | [7 empty] | # of Panel Required (Based on average 320 Watts per Panel) | Sqauare Footage Needed (Based on 3'x5' Panel) | A-CFA | 0.793 | 0.621 | 0.628 | 0.586 | 0.585 | 0.594 | 0.572 | 0.586 | 0.613 | 0.627 | 0.836 | 0.613 | 0.894 | 0.741 | 1.56 | 0.59
Conditioned Floor Area (CFA) | Climate Zone: | A: | # of Dwelling Units (NDU): | B: | Total PV Required in kW (kWPV): |  |  |  |  | B-Dwelling Units | 1.27 | 1.22 | 1.12 | 1.21 | 1.06 | 1.23 | 1.15 | 1.37 | 1.36 | 1.41 | 1.44 | 1.4 | 1.51 | 1.26 | 1.47 | 1.22
1410 | 13 | 0.894 | 1 | 1.51 | 2.7705 |  |  | 8.6579 | 129.8691
Photovoltiac Direct Current Size (SARA) | [6 empty] | Factor for Slope
Solar Acces Roof Area (SARA) | Total PV Required in kW (kWPV): |  |  | Roof Slope in Inches: | 0.25 | : 12 | 14
310 | 4.34
Is Battery Energy Storage System (BESS) Provided? |  |  |  | Required Size of PV
No |  |  |  | 2.7705