## Manual Fire Alarm
Manual Fire Alarm Requirements (IBC, Section 907)
Occupancy Type: | Requirement(s): | Exception(s):
Assembly (A-1, A-2, A-3, A-4, A-5) | All with an occupant load of 300 or greater; or, occupant load over 100 above / below lowest level of exit discharge (907.2.1) | Building equipped throughout with an NFPA 13 automatic sprinkler system and occupant notificaiton devices.
Buisiness (B) | Occupant load over 500; or, occupant load over 100 above/below lowest level of exit discharge; or, Group B fire areas containing an Ambulatory Care Facility (907.2.2) | Building equipped throughout with an NFPA 13 automatic sprinkler system and occupant notificaiton devices.
Educational (E) | Occupant load over 50 (907.2.3) | Occupant load is 50 or less
Factory (F-1, F-2) | F Occupancy is 3 stories or greater and has an occupant load of 500 above/below lowest level of exit discharge (907.2.4) | Building equipped throughout with an NFPA 13 automatic sprinkler system and occupant notificaiton devices.
Factory (F-1, F-2) | Manufacturing involving lithium-ion or lithium metal batteries (907.2.4.1 - 2024 IBC Only) | N/A
High Hazard (H) | Group H5 and in occupancies used for the manufacture of organic coatings. An automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers (907.2.5) | N/A
Institutional (I-1, I-2, I-3, I-4) | All I occupancies (907.2.6); In addition, automatic smoke detection system is required for the following: 907.2.6.1 (I-1), 907.2.6.2 (I-2), 907.2.6.3 (I-3) | I-1 & I-2 shall not be required at exits if located at all care provider's control stations or other constantly attended staff locations (note alarm boxes must be visible and not exceed travel distance per 907.4.2.1)
Mercantile (M) | All with an occupant load of 500 or greater; or, occupant load over 100 above / below lowest level of exit discharge (907.2.7) (907.2.7.1 - 2024 IBC / 2026 CBC) | Building equipped throughout with an NFPA 13 automatic sprinkler system and occupant notificaiton devices.
Mercantile (M) | Storage of lithium-ion or lithium metal batteries (907.2.7.2 - 2024 IBC Only) | N/A
Residential (R-1) | All R-1 (907.2.8.1) | Building equipped throughout with an NFPA 13 or NFPA 13R automatic sprinkler system and occupant notificaiton devices and min. one manual alarm box is still provided
Residential (R-2) | Any Dwelling/Sleeping unit located above / below lowest level of exit discharge; or, building contains more than 16 dwelling / sleeping units (907.2.9.1) | Building equipped throughout with an NFPA 13 or NFPA 13R automatic sprinkler system and occupant notificaiton devices.
Storage (S) (2024 IBC Only) | Public- and self-storage occupancies; 3 stories or greataer in height. Alarm required in all interior corridors (907.2.10.1) | N/A
Storage (S) (2024 IBC Only) | Storage of lithium-ion or lithium metal batteries (907.2.10.2) | N/A
Notes:
1. Sections are based on the 2021 & 2024 IBC. Requirements are the same for 2018 IBC. 2022 CBC, & 2025 CBC.
2. When building has a mixed occupancy, the most stringent requirement must be met throughout.
3. Requirements may also be subject to local fire official / Fire Marshall.
4. Listed exceptions are going to be the most common. Additional exceptions may apply (See respective Sections).

## Smoke Detection
Single - and Multiple-station Smoke Alarms (IBC, Section 907.2.11 & NFPA 72)
Occupancy Type: | Location(s):
Group R-1 | In sleeping areas, and in every room in the path of means of egress from sleeping area to other door leading form the sleeping unit (907.2.11.1)
Groups R-2, R-3, R-4, and I-1 | In each room used for sleeping purposes, and outside of each separate sleeping area in the immediate vicinity of bedrooms (907.2.11.2)
Misc | Installation near cooking appliances, Smoke arlarms shall be installed not less then 10' horizontally from a permanently installed cooking applicance. (907.2.11.3) - Exception, not less than 6' in Groups R-1, R-2, R-3, R-4, and I-1 occupancies
Notes:
1. Manual Alarm box must be within 5' from entrance / exit. In buildings without NFPA 13 or 13R sprinkler system, travel distance to nearest box cannot exceed 5'. (907.4.2.1)
2. Height of manual fire alarm shall be not less than 42" and not more than 48" from finished floor. (907.4.2.2)
3. Manual fire alarm boxes shall be provided with ready access, unobstructed, unobscured and visible at all times. (907.4.2.6)
4. When duct smoke detectors are supplied / required, it shall be connected to the buildings FACP (when fire alarm is required). (907.3.1)