## HVAC Reference (hidden)
BARD WALL MOUNT OUTDOOR AIR VENTILATION: |  |  |  |  | DAIKIN ROOF TOP OUTDOOR AIR VENTILATION: |  |  |  |  | Marvair WALL MOUNT OUTDOOR AIR VENTILATION:
HVAC SIZE: | SYSTEM CFM OUTPUT: | FAD | CRV | ECONOMIZER | HVAC SIZE: | SYSTEM CFM OUTPUT: | FAD | CRV | ECONOMIZER | HVAC SIZE: | SYSTEM CFM OUTPUT: | FAD | CRV | ECONOMIZER
N/A | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
1 TON | 420 | 105 | 210 | 420 | 2 TON | 780 | 195 | 390 | 780 | 1.5 TON | 660 | 99 | 330 | 660
1.5 TON | 600 | 150 | 300 | 600 | 2.5 TON | 900 | 225 | 450 | 900 | 2 TON | 850 | 127.5 | 425 | 850
2 TON | 800 | 200 | 400 | 800 | 3 TON | 1195 | 298.75 | 597.5 | 1195 | 2.5 TON | 1070 | 160.5 | 535 | 1070
2.5 TON | 950 | 237.5 | 475 | 950 | 3.5 TON | 1420 | 355 | 710 | 1420 | 3 TON | 1200 | 180 | 600 | 1200
3 TON | 1150 | 287.5 | 575 | 1150 | 4 TON | 1605 | 401.25 | 802.5 | 1605 | 3.5 TON | 1250 | 187.5 | 625 | 1250
3.5 TON | 1350 | 337.5 | 675 | 1350 | 5 TON | 1700 | 425 | 850 | 1700 | 4 TON | 1400 | 210 | 700 | 1400
4 TON | 1550 | 387.5 | 775 | 1550 | [5 empty] | 5 TON | 1750 | 262.5 | 875 | 1750
5 TON | 1750 | 437.5 | 875 | 1750
THRU-WALL ERV
HVAC SIZE: | SYSTEM CFM OUTPUT:
N/A | 0
THRU-WALL ERV | 30

## Natural Ventilation Calc
NATURAL VENTILATION CALCULATION: |  |  |  | Code: | IMC
C403.2.5 DOAS |  |  |  | Building Sq. Ft.: | 1400
|  |  |  | Is DOAS provided for Washington? | Yes
NATURAL VENTILATION PER IMC SECTION 402 (4% OF FLOOR AREA)
1400 | SQ. FT. X 4% = | 56 | SQ. FT. REQUIRED | Windows
|  |  |  | QTY: | Type of Window: | Width (Inches): | Height (Inches): | Total SQ. FT. of Glazing: | Operable Sq. Ft.:
NET TOTAL OF WINDOW OPENING(S) = 5.4 SQ. FT. PROVIDED |  |  |  | 1 | V.S. | 48 | 36 | 12 | 5.4
|  |  |  | 0 | V.S. | 0 | 0 | 0 | 0
|  |  |  | 0 | V.S. | 0 | 0 | 0 | 0
NET TOTAL OF DOOR OPENING(S) = 20 SQ. FT. PROVIDED |  |  |  | 0 | V.S. | 0 | 0 | 0 | 0
|  |  |  | 0 | V.S. | 0 | 0 | 0 | 0
|  |  |  | 0 | V.S. | 0 | 0 | 0 | 0
TOTAL 25.4 SQ.FT. OF WINDOW AND DOOR OPENINGS PROVIDED |  |  |  | Total: |  |  |  | 12 | 5.4
Doors
--->> |  |  |  | QTY: | Type of Door: | Width (Inches): | Height (Inches): | Total SQ. FT. of Doors: | Operable Sq. Ft.:
|  |  |  | 1 | Swinging | 36 | 80 | 20 | 20
COPY ABOVE AND "PASTESPEC" INTO AUTOCAD |  |  |  | 0 | Swinging | 0 | 0 | 0 | 0
|  |  |  | 0 | Swinging | 0 | 0 | 0 | 0
|  |  |  | 0 | Swinging | 0 | 0 | 0 | 0
|  |  |  | 0 | Swinging | 0 | 0 | 0 | 0
|  |  |  | 0 | Swinging | 0 | 0 | 0 | 0
|  |  |  | Total: |  |  |  | 20 | 20
[7 empty] | Total of Windows & Doors: |  | 25.4

## 2009 - 2021 IMC-UMC Single Zone
Use | FRESH AIR CALCULATION
OFFICES: | OFFICE SPACE | Floor Area (Az): | 0 | <--Enter Sq. Ft.
------->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | PEOPLE OUTDOOR FLOW RATE (Rp): |  | 5 |  |  | Type of HVAC: | BARD |  | N/A:
| AREA OUTDOOR FLOW RATE (Ra): |  | 0.06 | [5 empty] | OFFICES:
| OCCUPANT LOAD DENSITY / 1000 SQ. FT.: |  | 5 |  | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | PUBLIC USES:
| OCCUPANT LOAD OF SPACE (Pz): |  | 0 |  | 3 TON | 1 | FAD | 287.5 | EDUCATION:
| OUTDOOR AIR REQUIRED (Vbz=RpPz+RaAz): |  | 0 |  | 4 TON | 0 | FAD | 0 | WORK ROOMS:
| TOTAL FRESH AIR SUPPLIED: |  | 287.5 |  | 5 TON | 0 | FAD | 0 | HOTELS, MOTELS, RESORTS AND DORMATORIES:
| RESULTS: | 287.5 CFM > 0 CFM, THEREFORE OK | [6 empty] | RETAIL STORES, SALES FLOOR AND SHOWROOM FLOORS:
FOOD AND BEVERAGE SERVICE:
[5 empty] | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | DRY CLEANERS, LAUNDRIES:
SPORTS AND AMUSEMENT:
| VALUE(S) ABOVE CAN BE FOUND IN: | [7 empty] | STORAGE:
| IMC: | Table 403.3.1.1 / Zone Calc: Section 403.3.1.1.1.1 | [6 empty] | THEATERS:
| UMC: | Table 402.1 / Zone Calc: Section 403.2.1 | [6 empty] | SPECIALTY SHOPS:
| ASHREA: | Table 6-1 / Zone Calc: Section 6.2.4.1 | [6 empty] | TRANSPORTATION:
CORRECTIONAL FACILITIES:

## 2009 - 2021 IMC-UMC Multi-Zone
FRESH AIR CALCULATION
USE: | SPACE: | SQUARE FOOTAGE OF AREA (Az): | PEOPLE OUTDOOR FLOW RATE (Rp): | AREA OUTDOOR FLOW RATE (Ra): | OCCUPANT DENSITY /1000 sq. ft.: | OCCUPANT LOAD OF SPACE (Pz) | OUTDOOR AIR REQUIRED (Vbz=RpPz+RaAz):
OFFICES: | OFFICE SPACE | 0 | 5 | 0.06 | 5 | 0 | 0 |  | Type of HVAC: | BARD |  | N/A:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | OFFICES:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | PUBLIC USES:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 3 TON | 1 | FAD | 287.5 | EDUCATION:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | FAD | 0 | WORK ROOMS:
------->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | TOTAL OUTDOOR AIR REQUIRED: |  | 0 | RESULTS: |  | 287.5 CFM > 0 CFM, THEREFORE OK |  | N/A | 0 | FAD | 0 | HOTELS, MOTELS, RESORTS AND DORMATORIES:
| TOTAL FRESH AIR SUPPLIED: |  | 287.5 |  |  |  |  | N/A | 0 | FAD | 0 | RETAIL STORES, SALES FLOOR AND SHOWROOM FLOORS:
[8 empty] | N/A | 0 | FAD | 0 | FOOD AND BEVERAGE SERVICE:
DRY CLEANERS, LAUNDRIES:
SPORTS AND AMUSEMENT:
|  | VALUE(S) ABOVE CAN BE FOUND IN: | [5 empty] | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | STORAGE:
|  | IMC: | Table 403.3.1.1 / Zone Calc: Section 403.3.1.1.1.1 | [8 empty] | THEATERS:
|  | UMC: | Table 402.1 / Zone Calc: Section 403.2.1 | [8 empty] | SPECIALTY SHOPS:
|  | ASHREA 62.1: | Table 6-1 / Zone Calc: Section 6.2.4.1 | [8 empty] | TRANSPORTATION:
CORRECTIONAL FACILITIES:

## 2024 IMC-UMC Single
Use | FRESH AIR CALCULATION
Offices: | Office spaces | Floor Area (Az): | 0 | <--Enter Sq. Ft.
------->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | PEOPLE OUTDOOR FLOW RATE (Rp): |  | 5 |  |  | Type of HVAC: | BARD |  | N/A:
| AREA OUTDOOR FLOW RATE (Ra): |  | 0.06 | [5 empty] | Animal facilities:
| OCCUPANT LOAD DENSITY / 1000 SQ. FT.: |  | 5 |  | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | Correction facilities:
| OCCUPANT LOAD OF SPACE (Pz): |  | 0 |  | 3 TON | 2 | FAD | 575 | Dry cleaners, laundries:
| OUTDOOR AIR REQUIRED (Vbz=RpPz+RaAz): |  | 0 |  | 4 TON | 0 | FAD | 0 | Education:
| TOTAL FRESH AIR SUPPLIED: |  | 575 |  | 4 TON | 0 | FAD | 0 | Food and beverage service:
| RESULTS: | 575 CFM > 0 CFM, THEREFORE OK | [6 empty] | Hotels, motels, resorts and domitories:
Offices:
[5 empty] | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | Outpatien healthcar facilities:
Public spaces:
| VALUE(S) ABOVE CAN BE FOUND IN: | [7 empty] | Retial stores, sales floors, and show room floors:
| IMC: | Table 403.3.1.1 / Zone Calc: Section 403.3.1.1.1.1 | [6 empty] | Specialty shops:
| UMC: | Table 402.1 / Zone Calc: Section 403.2.1 | [6 empty] | Sports and amusement:
| ASHREA: | Table 6-1 / Zone Calc: Section 6.2.4.1 | [6 empty] | Storage:
Theaters:
Transportation:
Workrooms:

## 2024 IMC-UMC Multi-Zone
FRESH AIR CALCULATION
USE: | SPACE: | SQUARE FOOTAGE OF AREA (Az): | PEOPLE OUTDOOR FLOW RATE (Rp): | AREA OUTDOOR FLOW RATE (Ra): | OCCUPANT DENSITY /1000 sq. ft.: | OCCUPANT LOAD OF SPACE (Pz) | OUTDOOR AIR REQUIRED (Vbz=RpPz+RaAz):
OFFICES: | Office spaces | 0 | 5 | 0.06 | 5 | 0 | 0 |  | Type of HVAC: | BARD |  | N/A:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Animal facilities:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | Correction facilities:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 3 TON | 1 | FAD | 287.5 | Dry cleaners, laundries:
N/A: | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 1 | FAD | 0 | Education:
------->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | TOTAL OUTDOOR AIR REQUIRED: |  | 0 | RESULTS: |  | 287.5 CFM > 0 CFM, THEREFORE OK |  | N/A | 0 | FAD | 0 | Food and beverage service:
| TOTAL FRESH AIR SUPPLIED: |  | 287.5 |  |  |  |  | N/A | 0 | FAD | 0 | Hotels, motels, resorts and domitories:
[8 empty] | N/A | 0 | FAD | 0 | Offices:
Outpatien healthcar facilities:
Public spaces:
|  | VALUE(S) ABOVE CAN BE FOUND IN: | [5 empty] | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | Retial stores, sales floors, and show room floors:
|  | IMC: | Table 403.3.1.1 / Zone Calc: Section 403.3.1.1.1.1 | [8 empty] | Specialty shops:
|  | UMC: | Table 402.1 / Zone Calc: Section 403.2.1 | [8 empty] | Sports and amusement:
|  | ASHREA 62.1: | Table 6-1 / Zone Calc: Section 6.2.4.1 | [8 empty] | Storage:
Theaters:
Transportation:
Workrooms:

## Calculation Tables (hidden)
2009 - 2021 IMC |  |  |  |  | N/A | 0 | 2022 CEC SINGLE ZONE TABLE |  | N/A | 0 | 2022 CEC MULTI-ZONE TABLE |  | 2024 IMC |  |  |  | N/A | 0 | 2025 CEC SINGLE (Ra x Az) |  | N/A | 0 | 2025 CEC MULTI-ZONE (Ra x Az) |  | N/A | 0 | 2025 CEC SINGLE ZONE (Rp x Pz) |  | N/A | 0 | 2025 CEC MULTI ZONE (Rp x Pz)
BUILDING USE: | PEOPLE OUTDOOR FLOW RATE (Rp): | AREA OUTDOOR FLOW RATE (Ra): | OCCUPANT DENSITY /1000 sq. ft.: |  | (Educational Facilities:) |  |  |  | (Educational Facilities:) |  |  |  | BUILDING USE: | OCCUPANT DENSITY /1000 sq. ft.: | PEOPLE OUTDOOR FLOW RATE (Rp): | AREA OUTDOOR FLOW RATE (Ra): | (Educational Facilities:) |  |  |  | (Educational Facilities:) |  |  |  | (Educational Facilities:) |  |  |  | (Educational Facilities:)
N/A | 0 | 0 | 0 |  | Daycare (through age 4) | 0.15 |  | Title 24: CO2 Sensor required | Daycare (through age 4) | 0.15 |  | Title 24: CO2 Sensor required | N/A | 0 | 0 | 0 | Daycare (through age 4) | 0.15 | 210 | Title 24: CO2 Sensor required | Daycare (through age 4) | 0.15 |  |  | Daycare (through age 4) | 14 | 294 | Title 24: CO2 Sensor required | Daycare (through age 4) | 14 | 0 | Title 24: CO2 Sensor required
(OFFICES:) |  |  |  |  | Daycare sickroom | 0.15 |  |  | Daycare sickroom | 0.15 |  |  | ANIMAL FACILITIES: |  |  |  | Daycare sickroom | 0.15 | 210 |  | Daycare sickroom | 0.15 |  |  | Daycare sickroom | 5 | 105 |  | Daycare sickroom | 5 | 0
OFFICE SPACE | 5 | 0.06 | 5 |  | Classrooms (ages 5-8) | 0.15 |  | Title 24: CO2 Sensor required | Classrooms (ages 5-8) | 0.15 |  | Title 24: CO2 Sensor required | Animal exam room (Vet Office) | 20 | 10 | 0.12 | Classrooms (ages 5-8) | 0.15 | 210 | Title 24: CO2 Sensor required | Classrooms (ages 5-8) | 0.15 |  | Title 24: CO2 Sensor required | Classrooms (ages 5-8) | 25 | 525 | Title 24: CO2 Sensor required | Classrooms (ages 5-8) | 25 | 0 | Title 24: CO2 Sensor required
CONFERENCE ROOM(S) | 5 | 0.06 | 50 |  | Classrooms (ages 9-18) | 0.15 |  | Title 24: CO2 Sensor required | Classrooms (ages 9-18) | 0.15 |  | Title 24: CO2 Sensor required | Animal imaging (MR/CT/PET) | 20 | 10 | 0.18 | Classrooms (ages 9-18) | 0.15 | 210 | Title 24: CO2 Sensor required | Classrooms (ages 9-18) | 0.15 |  | Title 24: CO2 Sensor required | Classrooms (ages 9-18) | 25 | 525 | Title 24: CO2 Sensor required | Classrooms (ages 9-18) | 25 | 0 | Title 24: CO2 Sensor required
RECEPTION AREA | 5 | 0.06 | 30 |  | Lecture/postsecondary classroom | 0.15 |  | Title 24: CO2 Sensor required | Lecture/postsecondary classroom | 0.15 |  | Title 24: CO2 Sensor required | Animal operating rooms | 20 | 10 | 0.18 | Lecture/postsecondary classroom | 0.15 | 210 | Title 24: CO2 Sensor required | Lecture/postsecondary classroom | 0.15 |  | Title 24: CO2 Sensor required | Lecture/postsecondary classroom | 25 | 525 | Title 24: CO2 Sensor required | Lecture/postsecondary classroom | 25 | 0 | Title 24: CO2 Sensor required
MAIN ENRTY LOBBIES | 5 | 0.06 | 10 |  | Lecture hall (fixed seats) | 0.15 |  | Title 24: CO2 Sensor required | Lecture hall (fixed seats) | 0.15 |  | Title 24: CO2 Sensor required | Aniaml postoperative revovery room | 20 | 10 | 0.18 | Lecture hall (fixed seats) | 0.15 | 210 | Title 24: CO2 Sensor required | Lecture hall (fixed seats) | 0.15 |  | Title 24: CO2 Sensor required | Lecture hall (fixed seats) | 71 | 1491 | Title 24: CO2 Sensor required | Lecture hall (fixed seats) | 71 | 0 | Title 24: CO2 Sensor required
TELEPHONE / DATA ENRTY | 5 | 0.06 | 60 |  | Art classroom | 0.15 |  |  | Art classroom | 0.15 |  |  | Animal preparation rooms | 20 | 10 | 0.18 | Art classroom | 0.15 | 210 |  | Art classroom | 0.15 |  |  | Art classroom | 25 | 525 |  | Art classroom | 25 | 0
[5 empty] | Science laboratories | 0.15 |  |  | Science laboratories | 0.15 |  |  | Animal procdure rooms | 20 | 10 | 0.18 | Science laboratories | 0.15 | 210 |  | Science laboratories | 0.15 |  |  | Science laboratories | 25 | 525 |  | Science laboratories | 25 | 0
(PUBLIC USES:) |  |  |  |  | University/college laboratories | 0.15 |  |  | University/college laboratories | 0.15 |  |  | Animal surgery scrub | 20 | 10 | 0.18 | University/college laboratories | 0.15 | 210 |  | University/college laboratories | 0.15 |  |  | University/college laboratories | 25 | 525 |  | University/college laboratories | 25 | 0
CORRIDORS | 0 | 0.06 | 0 |  | Wood/metal shop | 0.15 |  |  | Wood/metal shop | 0.15 |  |  | Large-animal holding room | 20 | 10 | 0.18 | Wood/metal shop | 0.15 | 210 |  | Wood/metal shop | 0.15 |  |  | Wood/metal shop | 10 | 210 |  | Wood/metal shop | 10 | 0
COURTROOMS | 5 | 0.06 | 70 |  | Computer lab | 0.15 |  |  | Computer lab | 0.15 |  |  | Necropsy | 20 | 10 | 0.18 | Computer lab | 0.15 | 210 |  | Computer lab | 0.15 |  |  | Computer lab | 25 | 525 |  | Computer lab | 25 | 0
LEGISTLATIVE CHAMBERS | 5 | 0.06 | 50 |  | Media center | 0.15 |  |  | Media center | 0.15 |  |  | Small-animal cage room (static cages) | 20 | 10 | 0.18 | Media center | 0.15 | 210 |  | Media center | 0.15 |  |  | Media center | 25 | 525 |  | Media center | 25 | 0
LIBRARIES | 5 | 0.12 | 10 |  | Music/theater/dance | 0.15 |  | Title 24: CO2 Sensor required | Music/theater/dance | 0.15 |  | Title 24: CO2 Sensor required | Small-animal cage room (ventilated cages) | 20 | 10 | 0.18 | Music/theater/dance | 0.15 | 210 | Title 24: CO2 Sensor required | Music/theater/dance | 0.15 |  | Title 24: CO2 Sensor required | Music/theater/dance | 33 | 693 | Title 24: CO2 Sensor required | Music/theater/dance | 33 | 0 | Title 24: CO2 Sensor required
MUSEUMS / GALLERIES | 7.5 | 0.12 | 40 |  | Multiuse assembly | 0.15 |  | Title 24: CO2 Sensor required | Multiuse assembly | 0.15 |  | Title 24: CO2 Sensor required |  |  |  |  | Multiuse assembly | 0.15 | 210 | Title 24: CO2 Sensor required | Multiuse assembly | 0.15 |  | Title 24: CO2 Sensor required | Multiuse assembly | 33 | 693 | Title 24: CO2 Sensor required | Multiuse assembly | 33 | 0 | Title 24: CO2 Sensor required
RELIGIOUS WORSHIP | 5 | 0.06 | 120 | [9 empty] | CORRECTIONAL FACILITIES:
SMOKING LOUNGES | 60 | 0 | 70 |  | (Food and Beverage Service:) |  |  |  | (Food and Beverage Service:) |  |  |  | Booking/waiting | 50 | 7.5 | 0.06 | (Food and Beverage Service:) |  |  |  | (Food and Beverage Service:) |  |  |  | (Food and Beverage Service:) |  |  |  | (Food and Beverage Service:)
[5 empty] | Restaurant dining rooms | 0.15 |  | Title 24: CO2 Sensor required | Restaurant dining rooms | 0.15 |  | Title 24: CO2 Sensor required | Cells without plumbing | 25 | 5 | 0.12 | Restaurant dining rooms | 0.15 | 210 | Title 24: CO2 Sensor required | Restaurant dining rooms | 0.15 |  | Title 24: CO2 Sensor required | Restaurant dining rooms | 33 | 693 | Title 24: CO2 Sensor required | Restaurant dining rooms | 33 | 0 | Title 24: CO2 Sensor required
(EDUCATION:) |  |  |  |  | Cafeteria/fast-food dining | 0.15 |  | Title 24: CO2 Sensor required | Cafeteria/fast-food dining | 0.15 |  | Title 24: CO2 Sensor required | Cells with plumbing | 25 | 5 | 0.12 | Cafeteria/fast-food dining | 0.15 | 210 | Title 24: CO2 Sensor required | Cafeteria/fast-food dining | 0.15 |  | Title 24: CO2 Sensor required | Cafeteria/fast-food dining | 33 | 693 | Title 24: CO2 Sensor required | Cafeteria/fast-food dining | 33 | 0 | Title 24: CO2 Sensor required
CLASSROOM (5-8) | 10 | 0.12 | 25 |  | Bars, cocktail lounges | 0.2 |  | Title 24: CO2 Sensor required | Bars, cocktail lounges | 0.2 |  | Title 24: CO2 Sensor required | Day room | 30 | 5 | 0.06 | Bars, cocktail lounges | 0.5 | 700 |  | Bars, cocktail lounges | 0.5 |  |  | Bars, cocktail lounges | 33 | 693 |  | Bars, cocktail lounges | 33 | 0
CLASSROOM (9+) | 10 | 0.12 | 35 |  | Kitchen (cooking) | 0.15 |  |  | Kitchen (cooking) | 0.15 |  |  | Dining halls | 70 | 7.5 | 0.18 | Kitchen (cooking) | 0.15 | 210 |  | Kitchen (cooking) | 0.15 |  |  | Kitchen (cooking) | 3 | 63 |  | Kitchen (cooking) | 3 | 0
DAYCARE (UP TO 4YR) | 10 | 0.18 | 25 | [9 empty] | Guard stations | 15 | 5 | 0.06
ART CLASSROOM | 10 | 0.18 | 20 |  | (General:) |  |  |  | (General:) | [7 empty] | (General:) |  |  |  | (General:) |  |  |  | (General:) |  |  |  | (General:)
AUDITORIUMS | 5 | 0.06 | 150 |  | Break rooms | 0.15 |  | Title 24: CO2 Sensor required | Break rooms | 0.15 |  | Title 24: CO2 Sensor required | (DRY CLEANERS, LAUNDRIES:) |  |  |  | Break rooms | 0.15 | 210 | Title 24: CO2 Sensor required | Break rooms | 0.15 |  | Title 24: CO2 Sensor required | Break rooms | 33 | 693 | Title 24: CO2 Sensor required | Break rooms | 33 | 0 | Title 24: CO2 Sensor required
COMPUTER LAB | 10 | 0.12 | 25 |  | Coffee Stations | 0.15 |  | Title 24: CO2 Sensor required | Coffee Stations | 0.15 |  | Title 24: CO2 Sensor required | Coin-operated dry cleaner | 20 | 15 | 0 | Coffee Stations | 0.15 | 210 | Title 24: CO2 Sensor required | Coffee Stations | 0.15 |  | Title 24: CO2 Sensor required | Coffee Stations | 33 | 693 | Title 24: CO2 Sensor required | Coffee Stations | 33 | 0 | Title 24: CO2 Sensor required
LECTURE CLASSROOM | 7.5 | 0.06 | 65 |  | Conference/meeting | 0.15 |  | Title 24: CO2 Sensor required | Conference/meeting | 0.15 |  |  | Coin-operated laundries | 20 | 7.5 | 0.12 | Conference/meeting | 0.15 | 210 | Title 24: CO2 Sensor required | Conference/meeting | 0.15 |  |  | Conference/meeting | 33 | 693 | Title 24: CO2 Sensor required | Conference/meeting | 33 | 0 | Title 24: CO2 Sensor required
MEDIA CENTER | 10 | 0.12 | 25 |  | Corridors | 0.15 |  |  | Corridors | 0.15 |  | Title 24: CO2 Sensor required | Commercial dry cleaner | 30 | 30 | 0 | Corridors | 0.15 | 210 |  | Corridors | 0.15 |  | Title 24: CO2 Sensor required | Corridors | 5 | 105 |  | Corridors | 5 | 0
MULTIUSE ASSEMBLY | 7.5 | 0.06 | 100 |  | Occupiable storage rooms for liquids or gels | 0.15 |  |  | Occupiable storage rooms for liquids or gels | 0.15 |  |  | Commercial laundry | 10 | 5 | 0.12 | Occupiable storage rooms for liquids or gels | 0.15 | 210 |  | Occupiable storage rooms for liquids or gels | 0.15 |  |  | Occupiable storage rooms for liquids or gels | 2 | 42 |  | Occupiable storage rooms for liquids or gels | 2 | 0
MUSIC / THEATER / DANCE | 10 | 0.06 | 35 | [9 empty] | Storage, pick up | 30 | 7.5 | 0.12
SCIENCE LAB | 10 | 0.18 | 25 |  | (Hotels, Motels, Resorts, Dormitories:) |  |  |  | (Hotels, Motels, Resorts, Dormitories:) | [7 empty] | (Hotels, Motels, Resorts, Dormitories:) |  |  |  | (Hotels, Motels, Resorts, Dormitories:) |  |  |  | (Hotels, Motels, Resorts, Dormitories:) |  |  |  | (Hotels, Motels, Resorts, Dormitories:)
WOOD / METAL SHOP | 10 | 0.18 | 20 |  | Bedroom/living room | 0.15 |  |  | Bedroom/living room | 0.15 |  |  | (EDUCATION:) |  |  |  | Bedroom/living room | 0.15 | 210 |  | Bedroom/living room | 0.15 |  |  | Bedroom/living room | 3 | 63 |  | Bedroom/living room | 3 | 0
[5 empty] | Barracks sleeping areas | 0.15 |  |  | Barracks sleeping areas | 0.15 |  |  | Art classroom | 20 | 10 | 0.18 | Barracks sleeping areas | 0.15 | 210 |  | Barracks sleeping areas | 0.15 |  |  | Barracks sleeping areas | 5 | 105 |  | Barracks sleeping areas | 5 | 0
(WORKROOMS:) |  |  |  |  | Laundry rooms, central | 0.15 |  |  | Laundry rooms, central | 0.15 |  |  | Auditoriums | 150 | 5 | 0.06 | Laundry rooms, central | 0.15 | 210 |  | Laundry rooms, central | 0.15 |  |  | Laundry rooms, central | 5 | 105 |  | Laundry rooms, central | 5 | 0
BANK VAULTS / SAFE DEPOSIT | 5 | 0.06 | 5 |  | Laundry rooms within dwelling units | 0.15 |  |  | Laundry rooms within dwelling units | 0.15 |  |  | Classrooms (ages 5-8) | 25 | 10 | 0.12 | Laundry rooms within dwelling units | 0.15 | 210 |  | Laundry rooms within dwelling units | 0.15 |  |  | Laundry rooms within dwelling units | 5 | 105 |  | Laundry rooms within dwelling units | 5 | 0
COPY / PRINTING RM | 5 | 0.06 | 4 |  | Lobbies/pre-function | 0.15 |  | Title 24: CO2 Sensor required | Lobbies/pre-function | 0.15 |  | Title 24: CO2 Sensor required | Classrooms (ages 9 plus) | 35 | 10 | 0.12 | Lobbies/pre-function | 0.15 | 210 | Title 24: CO2 Sensor required | Lobbies/pre-function | 0.15 |  | Title 24: CO2 Sensor required | Lobbies/pre-function | 33 | 693 | Title 24: CO2 Sensor required | Lobbies/pre-function | 33 | 0 | Title 24: CO2 Sensor required
COMPUTER (WITHOUT PRINTING) | 5 | 0.06 | 4 |  | Multipurpose assembly | 0.5 |  |  | Multipurpose assembly | 0.5 |  |  | Computer lab | 25 | 10 | 0.12 | Multipurpose assembly | 0.15 | 210 |  | Multipurpose assembly | 0.15 |  |  | Multipurpose assembly | 33 | 693 |  | Multipurpose assembly | 33 | 0
PHARMACY PREP AREA | 5 | 0.18 | 10 | [9 empty] | Corridors | 0 | 0 | 0.06
PHOTO STUDIOS | 5 | 0.12 | 10 |  | (Office Buildings:) |  |  |  | (Office Buildings:) |  |  |  | Day care (through age 4) | 25 | 10 | 0.18 | (Office Buildings:) |  |  |  | (Office Buildings:) |  |  |  | (Office Buildings:) |  |  |  | (Office Buildings:)
MEAT PROCESSING | 15 | 0 | 10 |  | Breakrooms | 0.15 |  | Title 24: CO2 Sensor required | Breakrooms | 0.15 |  | Title 24: CO2 Sensor required | Lecture classroom | 65 | 7.5 | 0.06 | Breakrooms | 0.15 | 210 | Title 24: CO2 Sensor required | Breakrooms | 0.15 |  | Title 24: CO2 Sensor required | Breakrooms | 33 | 693 | Title 24: CO2 Sensor required | Breakrooms | 33 | 0 | Title 24: CO2 Sensor required
[5 empty] | Main entry lobbies | 0.15 |  | Title 24: CO2 Sensor required | Main entry lobbies | 0.15 |  | Title 24: CO2 Sensor required | Lecture hall (fixed seats) | 150 | 7.5 | 0.06 | Main entry lobbies | 0.15 | 210 | Title 24: CO2 Sensor required | Main entry lobbies | 0.15 |  | Title 24: CO2 Sensor required | Main entry lobbies | 33 | 693 | Title 24: CO2 Sensor required | Main entry lobbies | 33 | 0 | Title 24: CO2 Sensor required
(HOTELS, MOTELS, RESORTS AND DORMATORIES:) |  |  |  |  | Occupiable storage rooms for dry materials | 0.15 |  |  | Occupiable storage rooms for dry materials | 0.15 |  |  | Medfia center | 25 | 10 | 0.12 | Occupiable storage rooms for dry materials | 0.15 | 210 |  | Occupiable storage rooms for dry materials | 0.15 |  |  | Occupiable storage rooms for dry materials | 2 | 42 |  | Occupiable storage rooms for dry materials | 2 | 0
BEDROOM / LIVING ROOM | 5 | 0.06 | 10 |  | Office space | 0.15 |  |  | Office space | 0.15 |  |  | Multiuse assembly | 100 | 7.5 | 0.06 | Office space | 0.15 | 210 |  | Office space | 0.15 |  |  | Office space | 5 | 105 |  | Office space | 5 | 0
CONFERENCE / MEETING | 5 | 0.06 | 50 |  | Reception areas | 0.15 |  |  | Reception areas | 0.15 |  |  | Music/theater/dance | 35 | 10 | 0.06 | Reception areas | 0.15 | 210 |  | Reception areas | 0.15 |  |  | Reception areas | 5 | 105 |  | Reception areas | 5 | 0
DORMATORY SLEEPING AREAS | 5 | 0.06 | 20 |  | Telephone/data entry | 0.15 |  |  | Telephone/data entry | 0.15 |  |  | Science labortories | 25 | 10 | 0.18 | Telephone/data entry | 0.15 | 210 |  | Telephone/data entry | 0.15 |  |  | Telephone/data entry | 33 | 693 |  | Telephone/data entry | 33 | 0
LOBBIES / PREFUNCTION | 7.5 | 0.18 | 30 | [9 empty] | Smokeing loundes | 70 | 60 | 0
MULTIPURPOSE ASSEMBLY | 5 | 0.06 | 120 |  | (Miscellaneous Spaces:) |  |  |  | (Miscellaneous Spaces:) |  |  |  | Sports locker rooms | - | - | - | (Miscellaneous Spaces:) |  |  |  | (Miscellaneous Spaces:) |  |  |  | (Miscellaneous Spaces:) |  |  |  | (Miscellaneous Spaces:)
GAMBLING CASINOS | 7.5 | 0.18 | 120 |  | Bank vaults/safe deposit | 0.15 |  |  | Bank vaults/safe deposit | 0.15 |  |  | Wood/metal shops | 20 | 10 | 0.18 | Bank vaults/safe deposit | 0.15 | 210 |  | Bank vaults/safe deposit | 0.15 |  |  | Bank vaults/safe deposit | 5 | 105 |  | Bank vaults/safe deposit | 5 | 0
[5 empty] | Banks or bank lobbies | 0.15 |  |  | Banks or bank lobbies | 0.15 | [6 empty] | Banks or bank lobbies | 0.15 | 210 |  | Banks or bank lobbies | 0.15 |  |  | Banks or bank lobbies | 5 | 105 |  | Banks or bank lobbies | 5 | 0
(RETAIL STORES, SALES FLOOR AND SHOWROOM FLOORS:) |  |  |  |  | Computer (not printing) | 0.15 |  |  | Computer (not printing) | 0.15 |  |  | (FOOD AND BEVERAGE SERVICE:) |  |  |  | Computer (not printing) | 0.15 | 210 |  | Computer (not printing) | 0.15 |  |  | Computer (not printing) | 5 | 105 |  | Computer (not printing) | 5 | 0
SALES | 7.5 | 0.12 | 15 |  | Freezer and refrigerated spaces (<50F) | - |  |  | Freezer and refrigerated spaces (<50F) | - |  |  | Bars, cocktail lounges | 100 | 7.5 | 0.18 | Freezer and refrigerated spaces (<50F) | 0 | 0 |  | Freezer and refrigerated spaces (<50F) | 0 |  |  | Freezer and refrigerated spaces (<50F) | 0 | 0 |  | Freezer and refrigerated spaces (<50F) | 0 | 0
STORAGE ROOMS | 0 | 0.12 | 0 |  | General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  |  | General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  |  | Break rooms | 25 | 5 | 0.06 | General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 210 |  | General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  |  | General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 105 |  | General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0
WAREHOUSES | 10 | 0.06 | 0 |  | Pharmacy (prep. Area) | 0.15 |  |  | Pharmacy (prep. Area) | 0.15 |  |  | Cafereria, fast food | 100 | 7.5 | 0.18 | Pharmacy (prep. Area) | 0.15 | 210 |  | Pharmacy (prep. Area) | 0.15 |  |  | Pharmacy (prep. Area) | 5 | 105 |  | Pharmacy (prep. Area) | 5 | 0
MALL COMMON AREAS | 7.5 | 0.06 | 40 |  | Photo studios | 0.15 |  |  | Photo studios | 0.15 |  |  | Coffee stations | 20 | 5 | 0.06 | Photo studios | 0.15 | 210 |  | Photo studios | 0.15 |  |  | Photo studios | 5 | 105 |  | Photo studios | 5 | 0
SHIPPING AND RECEIVING | 10 | 0.12 | 2 |  | Shipping/receiving | 0.15 |  |  | Shipping/receiving | 0.15 |  |  | Corridors | 0 | 0 | 0.06 | Shipping/receiving | 0.15 | 210 |  | Shipping/receiving | 0.15 |  |  | Shipping/receiving | 2 | 42 |  | Shipping/receiving | 2 | 0
[5 empty] | Sorting, packing, light assembly | 0.15 |  |  | Sorting, packing, light assembly | 0.15 |  |  | Dining rooms | 70 | 7.5 | 0.18 | Sorting, packing, light assembly | 0.15 | 210 |  | Sorting, packing, light assembly | 0.15 |  |  | Sorting, packing, light assembly | 2 | 42 |  | Sorting, packing, light assembly | 2 | 0
(FOOD AND BEVERAGE SERVICE:) |  |  |  |  | Telephone closets | 0.15 |  |  | Telephone closets | 0.15 |  |  | Kitchen (cooking) | 20 | 7.5 | 0.12 | Telephone closets | 0.15 | 210 |  | Telephone closets | 0.15 |  |  | Telephone closets | 5 | 105 |  | Telephone closets | 5 | 0
DINING ROOM | 7.5 | 0.18 | 70 |  | Transportation waiting | 0.15 |  | Title 24: CO2 Sensor required | Transportation waiting | 0.15 |  | Title 24: CO2 Sensor required | Occupiable storage rooms for liquids or gels | 2 | 5 | 0.12 | Transportation waiting | 0.15 | 210 | Title 24: CO2 Sensor required | Transportation waiting | 0.15 |  | Title 24: CO2 Sensor required | Transportation waiting | 33 | 693 | Title 24: CO2 Sensor required | Transportation waiting | 33 | 0 | Title 24: CO2 Sensor required
CAFETERIA | 7.5 | 0.18 | 100 |  | Warehouses | 0.15 |  |  | Warehouses | 0.15 | [6 empty] | Warehouses | 0.15 | 210 |  | Warehouses | 0.15 |  |  | Warehouses | 1 | 21 |  | Warehouses | 1 | 0
KITCHENS (COOKING) | 7.5 | 0.12 | 20 |  | All others | 0.15 |  |  | All others | 0.15 |  |  | Hotels, motes, resorts, and dormitories |  |  |  | All others | 0.15 | 210 |  | All others | 0.15 |  |  | All others | 5 | 105 |  | All others | 5 | 0
BARS, COCKTAIL LOUNGES | 7.5 | 0.18 | 100 | [9 empty] | Bedroom/living room | 10 | 5 | 0.06
[5 empty] | (Public Assembly Spaces:) |  |  |  | (Public Assembly Spaces:) |  |  |  | Conference/meeting | 50 | 5 | 0.06 | (Public Assembly Spaces:) |  |  |  | (Public Assembly Spaces:) |  |  |  | (Public Assembly Spaces:) |  |  |  | (Public Assembly Spaces:)
(DRY CLEANERS, LAUNDRIES:) |  |  |  |  | Auditorium seating area | 0.15 |  | Title 24: CO2 Sensor required | Auditorium seating area | 0.15 |  | Title 24: CO2 Sensor required | Dormitory sleeping areas | 20 | 5 | 0.06 | Auditorium seating area | 0.15 | 0 | Title 24: CO2 Sensor required | Auditorium seating area | 0.15 |  | Title 24: CO2 Sensor required | Auditorium seating area | 71 | 1491 | Title 24: CO2 Sensor required | Auditorium seating area | 71 | 0 | Title 24: CO2 Sensor required
COIN-OPERATED DRY CLEANER | 15 | 0 | 20 |  | Places of religious worship | 0.15 |  | Title 24: CO2 Sensor required | Places of religious worship | 0.15 |  | Title 24: CO2 Sensor required | Gambling casinos | 120 | 7.5 | 0.18 | Places of religious worship | 0.15 | 210 | Title 24: CO2 Sensor required | Places of religious worship | 0.15 |  | Title 24: CO2 Sensor required | Places of religious worship | 71 | 1491 | Title 24: CO2 Sensor required | Places of religious worship | 71 | 0 | Title 24: CO2 Sensor required
COIN-OPERATED DRY LAUNDRIES | 7.5 | 0.12 | 20 |  | Courtrooms | 0.15 |  | Title 24: CO2 Sensor required | Courtrooms | 0.15 |  | Title 24: CO2 Sensor required | Laundry rooms, central | 10 | 5 | 0.12 | Courtrooms | 0.15 | 210 | Title 24: CO2 Sensor required | Courtrooms | 0.15 |  | Title 24: CO2 Sensor required | Courtrooms | 13 | 273 | Title 24: CO2 Sensor required | Courtrooms | 13 | 0 | Title 24: CO2 Sensor required
COMMERICAL DRY CLEANER | 30 | 0 | 30 |  | Legislative chambers | 0.15 |  | Title 24: CO2 Sensor required | Legislative chambers | 0.15 |  | Title 24: CO2 Sensor required | Laundry rooms within dwelling | 10 | 5 | 0.12 | Legislative chambers | 0.15 | 210 | Title 24: CO2 Sensor required | Legislative chambers | 0.15 |  | Title 24: CO2 Sensor required | Legislative chambers | 13 | 273 | Title 24: CO2 Sensor required | Legislative chambers | 13 | 0 | Title 24: CO2 Sensor required
COMMERICAL LAUNDRY | 5 | 0.12 | 10 |  | Libraries (reading rooms and stack areas) | 0.15 |  |  | Libraries (reading rooms and stack areas) | 0.15 |  |  | Lobbies/prefunction | 30 | 7.5 | 0.06 | Libraries (reading rooms and stack areas) | 0.15 | 210 |  | Libraries (reading rooms and stack areas) | 0.15 |  |  | Libraries (reading rooms and stack areas) | 10 | 210 |  | Libraries (reading rooms and stack areas) | 10 | 0
STORAGE, PICKUP | 7.5 | 0.12 | 30 |  | Lobbies | 0.15 |  | Title 24: CO2 Sensor required | Lobbies | 0.15 |  | Title 24: CO2 Sensor required | Multipurpose assembly | 120 | 5 | 0.06 | Lobbies | 0.15 | 210 | Title 24: CO2 Sensor required | Lobbies | 0.15 |  | Title 24: CO2 Sensor required | Lobbies | 33 | 693 | Title 24: CO2 Sensor required | Lobbies | 33 | 0 | Title 24: CO2 Sensor required
[5 empty] | Museums (children's) | 0.15 |  | Title 24: CO2 Sensor required | Museums (children's) | 0.15 |  | Title 24: CO2 Sensor required |  |  |  |  | Museums (children's) | 0.15 | 210 | Title 24: CO2 Sensor required | Museums (children's) | 0.15 |  | Title 24: CO2 Sensor required | Museums (children's) | 17 | 357 | Title 24: CO2 Sensor required | Museums (children's) | 17 | 0 | Title 24: CO2 Sensor required
(SPORTS AND AMUSEMENT:) |  |  |  |  | Museums/galleries | 0.15 |  | Title 24: CO2 Sensor required | Museums/galleries | 0.15 |  | Title 24: CO2 Sensor required | Offices |  |  |  | Museums/galleries | 0.15 | 210 | Title 24: CO2 Sensor required | Museums/galleries | 0.15 |  | Title 24: CO2 Sensor required | Museums/galleries | 17 | 357 | Title 24: CO2 Sensor required | Museums/galleries | 17 | 0 | Title 24: CO2 Sensor required
GYM, STADUIM, ARENA (PLAY AREA) | 7 | 0.18 | 7 | [9 empty] | Break rooms | 50 | 5 | 0.12
HEALTH CLUB / AEROBICS ROOM | 20 | 0.06 | 40 |  | (Residential:) |  |  |  | (Residential:) |  |  |  | Conference rooms | 50 | 5 | 0.06 | (Residential:) |  |  |  | (Residential:) |  |  |  | (Residential:) |  |  |  | (Residential:)
HEALTH CLUB / WEIGHT ROOM | 20 | 0.06 | 10 |  | Common corridors | 0 |  |  | Common corridors | 0 |  |  | Main enrty lobbies | 10 | 5 | 0.06 | Common corridors | 0.15 | 210 |  | Common corridors | 0.15 |  |  | Common corridors | 5 | 105 |  | Common corridors | 5 | 0
GAME ARCADES | 7.5 | 0.18 | 20 | [9 empty] | Occupiable storage rooms for dry material | 2 | 5 | 0.06
DISCO / DANCE FLOORS | 20 | 0.06 | 100 |  | (Retail:) |  |  |  | (Retail:) |  |  |  | Office spaces | 5 | 5 | 0.06 | (Retail:) |  |  |  | (Retail:) |  |  |  | (Retail:) |  |  |  | (Retail:)
BOWLING ALLEYS | 10 | 0.12 | 40 |  | Sales (except as below) | 0.2 |  | Title 24: CO2 Sensor required | Sales (except as below) | 0.2 |  | Title 24: CO2 Sensor required | Reception areas | 30 | 5 | 0.06 | Sales (except as below) | 0.25 | 350 |  | Sales (except as below) | 0.25 |  |  | Sales (except as below) | 17 | 357 |  | Sales (except as below) | 17 | 0
SPECTATOR AREAS | 7.5 | 0.06 | 150 |  | Mall common areas | 0.15 |  | Title 24: CO2 Sensor required | Mall common areas | 0.15 |  | Title 24: CO2 Sensor required | Telephone/data entry | 60 | 5 | 0.06 | Mall common areas | 0.15 | 210 | Title 24: CO2 Sensor required | Mall common areas | 0.15 |  | Title 24: CO2 Sensor required | Mall common areas | 17 | 357 | Title 24: CO2 Sensor required | Mall common areas | 17 | 0 | Title 24: CO2 Sensor required
[5 empty] | Barbershop | 0.4 |  |  | Barbershop | 0.4 | [6 empty] | Barbershop | 0.4 | 560 |  | Barbershop | 0.4 |  |  | Barbershop | 17 | 357 |  | Barbershop | 17 | 0
(STORAGE:) |  |  |  |  | Beauty and nail salons | 0.4 |  |  | Beauty and nail salons | 0.4 |  |  | Outpatient healthcare facilities |  |  |  | Beauty and nail salons | 0.4 | 560 |  | Beauty and nail salons | 0.4 |  |  | Beauty and nail salons | 17 | 357 |  | Beauty and nail salons | 17 | 0
REFRIGERATED WAREHOUSES / FREEZERS | 10 | 0 | 0 |  | Pet shops (animal areas) | 0.15 |  | Title 24: CO2 Sensor required | Pet shops (animal areas) | 0.15 |  | Title 24: CO2 Sensor required | Birthing room | 15 | 10 | 0.18 | Pet shops (animal areas) | 0.2 | 280 |  | Pet shops (animal areas) | 0.2 |  |  | Pet shops (animal areas) | 17 | 357 |  | Pet shops (animal areas) | 17 | 0
WAREHOUSES | 10 | 0.06 | 0 |  | Supermarket | 0.2 |  | Title 24: CO2 Sensor required | Supermarket | 0.2 |  | Title 24: CO2 Sensor required | Class 1 imaging room | 5 | 5 | 0.12 | Supermarket | 0.25 | 350 |  | Supermarket | 0.25 |  |  | Supermarket | 17 | 357 |  | Supermarket | 17 | 0
[5 empty] | Coin-operated laundries | 0.3 |  |  | Coin-operated laundries | 0.3 |  |  | Dental operatory | 20 | 10 | 0.18 | Coin-operated laundries | 0.3 | 420 |  | Coin-operated laundries | 0.3 |  |  | Coin-operated laundries | 17 | 357 |  | Coin-operated laundries | 17 | 0
(THEATERS:) | [12 empty] | General exam room | 20 | 7.5 | 0.12
LOBBIES | 5 | 0.06 | 150 |  | (Sports and Entertainment:) |  |  |  | (Sports and Entertainment:) |  |  |  | Other dental treatment areas | 5 | 5 | 0.06 | (Sports and Entertainment:) |  |  |  | (Sports and Entertainment:) |  |  |  | (Sports and Entertainment:) |  |  |  | (Sports and Entertainment:)
STAGES, STUDIOS | 10 | 0.06 | 70 |  | Gym, sports arena (play area) | 0.15 |  | Title 24: CO2 Sensor required | Gym, sports arena (play area) | 0.15 |  | Title 24: CO2 Sensor required | Physical therapy exercise areas | 7 | 20 | 0.18 | Gym, sports arena (play area) | 0.15 | 345 | Title 24: CO2 Sensor required | Gym, sports arena (play area) | 0.15 |  | Title 24: CO2 Sensor required | Gym, sports arena (play area) | 10 | 210 | Title 24: CO2 Sensor required | Gym, sports arena (play area) | 10 | 0 | Title 24: CO2 Sensor required
TICKET BOOTHS | 5 | 0.06 | 60 |  | Spetator areas | 0.15 |  | Title 24: CO2 Sensor required | Spetator areas | 0.15 |  | Title 24: CO2 Sensor required | Physical therapy individual room | 20 | 10 | 0.06 | Spetator areas | 0.15 | 210 | Title 24: CO2 Sensor required | Spetator areas | 0.15 |  | Title 24: CO2 Sensor required | Spetator areas | 33 | 693 | Title 24: CO2 Sensor required | Spetator areas | 33 | 0 | Title 24: CO2 Sensor required
[5 empty] | Swimming (pool) | 0.15 |  |  | Swimming (pool) | 0.15 |  |  | Physical therapeutic pool area | 0 | 0 | 0.48 | Swimming (pool) | 0.15 | 210 |  | Swimming (pool) | 0.15 |  |  | Swimming (pool) | 10 | 210 |  | Swimming (pool) | 10 | 0
(SPECIALTY SHOPS:) |  |  |  |  | Swimming (deck) | 0.15 |  | Title 24: CO2 Sensor required | Swimming (deck) | 0.15 |  | Title 24: CO2 Sensor required | Prosthestics and orthotics room | 20 | 10 | 0.18 | Swimming (deck) | 0.15 | 210 | Title 24: CO2 Sensor required | Swimming (deck) | 0.15 |  | Title 24: CO2 Sensor required | Swimming (deck) | 33 | 693 | Title 24: CO2 Sensor required | Swimming (deck) | 33 | 0 | Title 24: CO2 Sensor required
BARBER | 7.5 | 0.06 | 25 |  | Disco/dance floors | 0.15 |  | Title 24: CO2 Sensor required | Disco/dance floors | 0.15 |  | Title 24: CO2 Sensor required | Psychiatric consultation room | 20 | 5 | 0.06 | Disco/dance floors | 0.15 | 210 | Title 24: CO2 Sensor required | Disco/dance floors | 0.15 |  | Title 24: CO2 Sensor required | Disco/dance floors | 100 | 2100 | Title 24: CO2 Sensor required | Disco/dance floors | 100 | 0 | Title 24: CO2 Sensor required
BEAUTY SALONS | 20 | 0.12 | 25 |  | Health club/aerobics room | 0.15 |  |  | Health club/aerobics room | 0.15 |  |  | Psychiatric exam room | 20 | 5 | 0.06 | Health club/aerobics room | 0.15 | 0 |  | Health club/aerobics room | 0.15 |  |  | Health club/aerobics room | 10 | 210 |  | Health club/aerobics room | 10 | 0
NAIL SALONS | 20 | 0.12 | 25 |  | Health club/weight rooms | 0.15 |  |  | Health club/weight rooms | 0.15 |  |  | Psychiatric group room | 50 | 5 | 0.06 | Health club/weight rooms | 0.15 | 0 |  | Health club/weight rooms | 0.15 |  |  | Health club/weight rooms | 10 | 210 |  | Health club/weight rooms | 10 | 0
PET SHOPS (ANIMAL AREAS) | 7.5 | 0.18 | 10 |  | Bowling alley (seating) | 0.15 |  | Title 24: CO2 Sensor required | Bowling alley (seating) | 0.15 |  | Title 24: CO2 Sensor required | Psychiatric seclusion room | 5 | 10 | 0.06 | Bowling alley (seating) | 0.15 | 210 | Title 24: CO2 Sensor required | Bowling alley (seating) | 0.15 |  | Title 24: CO2 Sensor required | Bowling alley (seating) | 7 | 147 | Title 24: CO2 Sensor required | Bowling alley (seating) | 7 | 0 | Title 24: CO2 Sensor required
SUPERMARKETS | 7.5 | 0.06 | 8 |  | Gambling casinos | 0.15 |  | Title 24: CO2 Sensor required | Gambling casinos | 0.15 |  | Title 24: CO2 Sensor required | Speech therapy room | 20 | 5 | 0.06 | Gambling casinos | 0.15 | 210 | Title 24: CO2 Sensor required | Gambling casinos | 0.15 |  | Title 24: CO2 Sensor required | Gambling casinos | 45 | 945 | Title 24: CO2 Sensor required | Gambling casinos | 45 | 0 | Title 24: CO2 Sensor required
[5 empty] | Game arcades | 0.15 |  | Title 24: CO2 Sensor required | Game arcades | 0.15 |  | Title 24: CO2 Sensor required | Urgent care exam room | 20 | 7.5 | 0.12 | Game arcades | 0.15 | 210 | Title 24: CO2 Sensor required | Game arcades | 0.15 |  | Title 24: CO2 Sensor required | Game arcades | 45 | 945 | Title 24: CO2 Sensor required | Game arcades | 45 | 0 | Title 24: CO2 Sensor required
(TRANSPORTATION:) |  |  |  |  | Stages, studios | 0.15 |  | Title 24: CO2 Sensor required | Stages, studios | 0.15 |  | Title 24: CO2 Sensor required | Urgent care observation room | 20 | 5 | 0.06 | Stages, studios | 0.15 | 210 | Title 24: CO2 Sensor required | Stages, studios | 0.15 |  | Title 24: CO2 Sensor required | Stages, studios | 33 | 693 | Title 24: CO2 Sensor required | Stages, studios | 33 | 0 | Title 24: CO2 Sensor required
PLATFORMS | 7.5 | 0.06 | 100 | [9 empty] | Urgent care treatment room | 20 | 7.5 | 0.18
TRANSPORTATION WAITING | 7.5 | 0.06 | 100 | [9 empty] | Urgent care triage room | 20 | 10 | 0.18
[5 empty] | Space 1: | 0 |  |  | Space 1: | 0 | [6 empty] | Space 1: | 0 |  |  | Space 1: | 0 |  |  | Space 1: | 0 |  |  | Space 1: | 0
(CORRECTIONAL FACILITIES:) | [8 empty] | Space 2: | 0 |  |  | Public spaces | [7 empty] | Space 2: | 0 | [6 empty] | Space 2: | 0
BOOKING / WAITING | 7.5 | 0.06 | 50 | [5 empty] | Space 3: | 0 |  |  | Corridors | 0 | 0 | 0.06 |  |  |  |  | Space 3: | 0 | [6 empty] | Space 3: | 0
CELLS (W/O PLUMBING) | 5 | 0.12 | 25 | [5 empty] | Space 4: | 0 |  |  | Courtrooms | 70 | 5 | 0.06 |  |  |  |  | Space 4: | 0 | [6 empty] | Space 4: | 0
CELLS (W/ PLUMBING) | 5 | 0.12 | 25 | [5 empty] | Space 5: | 0 |  |  | Legislative chambers | 50 | 5 | 0.06 |  |  |  |  | Space 5: | 0 | [6 empty] | Space 5: | 0
DAY ROOM | 5 | 0.06 | 30 | [9 empty] | Libraries | 10 | 5 | 0.12
GUARD STATIONS | 5 | 0.06 | 15 | [9 empty] | Museums (children's) | 40 | 7.5 | 0.12
[13 empty] | Museums/galleries | 40 | 7.5 | 0.06
|  |  |  | 2024 IMC | [8 empty] | Places of religious worship | 120 | 5 | 0.06
N/A: |  |  |  | N/A: | [8 empty] | Smoking lounges | 70 | 60 | 0
OFFICES: |  |  |  | Animal facilities:
PUBLIC USES: |  |  |  | Correction facilities: | [8 empty] | Retail stores, sales floors and showroom floors
EDUCATION: |  |  |  | Dry cleaners, laundries: | [8 empty] | Mall common areas | 40 | 7.5 | 0.06
WORK ROOMS: |  |  |  | Education: | [8 empty] | Sales | 15 | 7.5 | 0.12
HOTELS, MOTELS, RESORTS AND DORMATORIES: |  |  |  | Food and beverage service: | [8 empty] | Shipping and receiving | 2 | 10 | 0.12
RETAIL STORES, SALES FLOOR AND SHOWROOM FLOORS: |  |  |  | Hotels, motels, resorts and domitories: | [8 empty] | Smoking lounges | 70 | 60 | 0
FOOD AND BEVERAGE SERVICE: |  |  |  | Offices: | [8 empty] | Storage rooms | 0 | 0 | 0.12
DRY CLEANERS, LAUNDRIES: |  |  |  | Outpatien healthcar facilities: | [8 empty] | Warehouses | 0 | 10 | 0.06
SPORTS AND AMUSEMENT: |  |  |  | Public spaces:
STORAGE: |  |  |  | Retial stores, sales floors, and show room floors: | [8 empty] | Specialty shops
THEATERS: |  |  |  | Specialty shops: | [8 empty] | Banks or lobbies | 15 | 7.5 | 0.06
SPECIALTY SHOPS: |  |  |  | Sports and amusement: | [8 empty] | Barber | 25 | 7.5 | 0.06
TRANSPORTATION: |  |  |  | Storage: | [8 empty] | Beauty salons | 25 | 20 | 0.12
CORRECTIONAL FACILITIES: |  |  |  | Theaters: | [8 empty] | Nail salons | 25 | 20 | 0.12
|  |  |  | Transportation: | [8 empty] | Pet shops (animal areas) | 10 | 7.5 | 0.18
|  |  |  | Workrooms: | [8 empty] | Supermarkets | 8 | 7.5 | 0.06
Sports and amusement
[13 empty] | Bowling alleys (seating areas) | 40 | 10 | 0.12
[13 empty] | Disco/dance floors | 100 | 20 | 0.06
[13 empty] | Gambling Casinos | 120 | 7.5 | 0.18
[13 empty] | Game arcades | 20 | 7.5 | 0.18
[13 empty] | Gym, stadium, arena (play area) | 7 | 20 | 0.18
[13 empty] | Health club/aerobics room | 40 | 20 | 0.06
[13 empty] | Health club/weight room | 10 | 20 | 0.06
[13 empty] | Ice arenas w/o combustions engines | 0 | 0 | 0.3
[13 empty] | Spectator areas | 150 | 7.5 | 0.06
[13 empty] | Swimming pools (pool and deck area) | 0 | 0 | 0.48
Storage
[13 empty] | Refrigerated warehouses/freezers | 0 | 10 | 0
[13 empty] | Warehouses | 0 | 10 | 0.06
Theaters
[13 empty] | Auditoriums | 150 | 5 | 0.06
[13 empty] | Lobbies | 150 | 5 | 0.06
[13 empty] | Stages, studios | 70 | 10 | 0.06
[13 empty] | Ticket booths | 60 | 5 | 0.06
Transportation
[13 empty] | Platforms | 100 | 7.5 | 0.06
[13 empty] | Transportation waiting | 100 | 7.5 | 0.06
Workrooms
[13 empty] | Bank vaults/safe deposit | 5 | 5 | 0.06
[13 empty] | Computer (w/o printing) | 4 | 5 | 0.06
[13 empty] | Copy, printing rooms | 4 | 5 | 0.06
[13 empty] | Manufacturing where hazardous materials are not used | 7 | 10 | 0.18
[13 empty] | Manufacturing where hazardous materials are used | 7 | 10 | 0.18
[13 empty] | Meat processing | 10 | 15 | 0
[13 empty] | Pharmacy (prep. Area) | 10 | 5 | 0.18
[13 empty] | Photo studios | 10 | 5 | 0.12
[13 empty] | Sorting, packing, light assembly | 7 | 7.5 | 0.12
[13 empty] | Telephone closets | 0 | 0 | 0

## 2022 CA Single Zone Calculator
USE: | FRESH AIR CALCULATION (Table 120.1-A & Section 120.1(c)(3))
Office Buildings: | Office space | Floor Area (Az): | 1400 | <--Enter Square Footage
------->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | MIN. VENTILATION AIR RATE FOR DCV (Ra): |  | 0.15 |  |  | Type of HVAC: | BARD
| OUTDOOR AIR REQUIRED: |  | 210
| TOTAL FRESH AIR SUPPLIED: |  | 2300 |  | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | Office Buildings:
| RESULTS: | 2300 CFM > 210 CFM, THEREFORE OK |  |  | 3 TON | 2 | ECONOMIZER | 2300 | Educational Facilities:
[5 empty] | N/A | 0 | FAD | 0 | General:
[5 empty] | N/A | 0 | FAD | 0 | Hotels, Motels, Resorts, Dormitories:
| VALUE(S) ABOVE CAN BE FOUND IN: | [7 empty] | Food and Beverage Service:
| CA Energy Code: | Table 120.1-A & Section 120.1(c)(3) | [6 empty] | Miscellaneous Spaces:
[5 empty] | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | Public Assembly Spaces:
Residential:
| CO2 Sensor Requirements: CA Energy Code Section 120.1(d)(3) |  |  |  | Breakrooms |  |  |  | Retail:
[5 empty] | Main entry lobbies |  |  |  | Sports and Entertainment:
Occupiable storage rooms for dry materials
Office space
Reception areas
Telephone/data entry

## 2022 CA Multi-Zone Calculator
FRESH AIR CALCULATION (Table 120.1-A & Section 120.1(c)(3))
USE: | SPACE | SQUARE FOOTAGE OF FREE ZONE AREA (Az): | MIN. VENTILATION AIR RATE FOR DCV (Ra):
Office Buildings: | Office space | 0 | 0.15 |  | Type of HVAC: | BARD
N/A: | N/A | 0 | 0 |  |  |  |  | N/A:
N/A: | N/A | 0 | 0 | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | Office Buildings:
N/A: | N/A | 0 | 0 | 3 TON | 2 | ECONOMIZER | 2300 | Educational Facilities:
N/A: | N/A | 0 | 0 | N/A | 0 | FAD | 0 | General:
---->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | OUTDOOR AIR REQUIRED: |  | 0 | N/A | 0 | FAD | 0 | Hotels, Motels, Resorts, Dormitories:
| TOTAL FRESH AIR SUPPLIED: |  | 2300 |  |  |  |  | Food and Beverage Service:
| RESULTS: | 2300 CFM > 0 CFM, THEREFORE OK | [5 empty] | Miscellaneous Spaces:
|  |  |  | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | Public Assembly Spaces:
Residential:
| VALUE(S) ABOVE CAN BE FOUND IN: | [6 empty] | Retail:
| CA Energy Code: | Table 120.1-A & Section 120.1(c)(3) | [5 empty] | Sports and Entertainment:
CO2 Sensor Requirements: CA Energy Code Section 120.1(d)(3)

## 2025 CA Single Zone Calculator
USE: | FRESH AIR CALCULATION (Table 120.1-A & Section 120.1(c)(3))
Office Buildings: | Office space | Floor Area (Az): | 1400 | <--Enter Square Footage | [5 empty] | Ra x Az = | 0.15 | 210
------->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | TOTAL OUTDOOR AIRFLOW RATE (Rt): |  | 0.15 | [6 empty] | Rp x Pz = | 5 | 75 | Using Occupant Load Density
|  |  |  | 9 | <--Enter Occupant Load |  |  |  |  | Rp x Pz = | 9 | 135 | Using Actual Occupant Load
| TOTAL OUTDOOR AIRFLOW RATE (Rt x Az): |  | 210 | [5 empty] | Office Buildings: |  |  | 135 | <-- Greater of Occ. Load Density & Actual Occupant Load
| TOTAL FRESH AIR SUPPLIED: |  | 2300 |  |  | Type of HVAC: | BARD |  | Educational Facilities:
| RESULTS: | 2300 CFM > 210 CFM, THEREFORE OK | [6 empty] | General:
[5 empty] | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | Hotels, Motels, Resorts, Dormitories:
| VALUE(S) ABOVE CAN BE FOUND IN: |  |  |  | 3 TON | 2 | ECONOMIZER | 2300 | Food and Beverage Service:
| CA Energy Code: | Table 120.1-A & Section 120.1(c)(3) |  |  | N/A | 0 | FAD | 0 | Miscellaneous Spaces:
[5 empty] | N/A | 0 | FAD | 0 | Public Assembly Spaces:
Residential:
| CO2 Sensor Requirements: CA Energy Code Section 120.1(d)(3) |  |  |  | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | Retail:
Sports and Entertainment:
Breakrooms
Main entry lobbies
Occupiable storage rooms for dry materials
Office space
Reception areas
Telephone/data entry

## 2025 CA Multi-Zone Calculator
FRESH AIR CALCULATION (Table 120.1-A & Section 120.1(c)(3))
USE: | SPACE | Floor Area (Az): | TOTAL OUTDOOR AIRFLOW RATE (Rt):
Office Buildings: | Office space | 1400 | 0.15 |  | 9 | <--Enter Occupant Load | [5 empty] | Use 1: | Ra x Az = | 0.15 | 210 |  | 210 | Sum of Ra X Az
N/A: | N/A | 0 | 0 |  | 0 | <--Enter Occupant Load |  |  |  |  | N/A: | Use 2: | Ra x Az = | 0 | 0
N/A: | N/A | 0 | 0 |  | 0 | <--Enter Occupant Load |  | Type of HVAC: | BARD |  | Office Buildings: | Use 3: | Ra x Az = | 0 | 0
N/A: | N/A | 0 | 0 |  | 0 | <--Enter Occupant Load |  |  |  |  | Educational Facilities: | Use 4: | Ra x Az = | 0 | 0
N/A: | N/A | 0 | 0 |  | 0 | <--Enter Occupant Load | HVAC SIZE: | # OF A/C's: | VENTILATION: | VENT RATE: | General: | Use 5: | Ra x Az = | 0 | 0
---->>>> DON'T COPY AND PASTE THIS PORTION ON PLANS | TOTAL OUTDOOR AIRFLOW RATE (Rt x Az): |  |  | 210 |  |  | 3 TON | 2 | ECONOMIZER | 2300 | Hotels, Motels, Resorts, Dormitories: | Use 1: | Rp x Pz = | 5 | 75 | Using Occupant Load Density | 75 | Sum of Occ Load Density
| TOTAL FRESH AIR SUPPLIED: |  |  | 2300 |  |  | N/A | 0 | FAD | 0 | Food and Beverage Service: | Use 2: | Rp x Pz = | 0 | 0 | Using Occupant Load Density
| RESULTS: |  | 2300 CFM > 210 CFM, THEREFORE OK |  |  |  | N/A | 0 | FAD | 0 | Miscellaneous Spaces: | Use 3: | Rp x Pz = | 0 | 0 | Using Occupant Load Density
[11 empty] | Public Assembly Spaces: | Use 4: | Rp x Pz = | 0 | 0 | Using Occupant Load Density
[11 empty] | Residential: | Use 5: | Rp x Pz = | 0 | 0 | Using Occupant Load Density
| VALUE(S) ABOVE CAN BE FOUND IN: | [5 empty] | FOR 100% OUTSIDE AIR, USE ECONOMIZER OPTION |  |  |  | Retail: | Use 1: | Rp x Pz = | 9 | 135 | Using Actual Occupant Load | 135 | Sum of Actual Occ Load
| CA Energy Code: | Table 120.1-A & Section 120.1(c)(3) | [8 empty] | Sports and Entertainment: | Use 2: | Rp x Pz = | 0 | 0 | Using Actual Occupant Load
[12 empty] | Use 3: | Rp x Pz = | 0 | 0 | Using Actual Occupant Load
[12 empty] | Use 4: | Rp x Pz = | 0 | 0 | Using Actual Occupant Load
| CO2 Sensor Requirements: CA Energy Code Section 120.1(d)(3) | [10 empty] | Use 5: | Rp x Pz = | 0 | 0 | Using Actual Occupant Load
[17 empty] | 135 | <-- Greater of Occ. Load Density & Actual Occupant Load

## 2009 - 2021 IMC Exhaust Rqmts
IMC Table 403.3.1.1
Occupancy Classification: | Exhaust Rate: | Square Footage: | # of Fixtures: | Exhaust CFM Required:
Correction Facilities:
Cells W/ Plumbing Fixtures: | 1 | 0 |  | 0
Education:
Art Classroom: | 0.7 | 0 |  | 0
Locker/Dressing Rooms: | 0.25 | 0 |  | 0
Science Laboratories: | 1 | 0 |  | 0
Sports Locker Rooms: | 0.5 | 0 |  | 0
Wood / Metal Shops: | 0.5 | 0 |  | 0
Food and Beverage:
Kitchens (cooking): | 0.7 | 0 |  | 0
Hotels, Motels, Resorts, and Dormatories:
Bathrooms/Toilet - Private: | 50 |  | 0 | 0
Private Dwellings, Single and Multiple:
Garages, common for multi units: | 0.75 | 0 |  | 0
Kitchens (Cont. running fan): | 50 |  | 0 | 0
Kitchens (Intermediate fan): | 100 |  | 0 | 0
Toilet Rooms and Bathrooms (Cont. running fan): | 25 |  | 0 | 0
Toilet Rooms and Bathrooms (Intermediate fan): | 50 |  | 0 | 0
Public Spaces:
Elevator Car: | 1 | 0
Shower room (per shower head) (Cont. running fan): | 20 |  | 0 | 0
Shower room (per shower head) (Intermediate fan): | 50 |  | 0 | 0
Toilet Rooms - Public (Cont. running fan): | 50 |  | 0 | 0
Toilet Rooms - Public (Intermediate fan): | 70 |  | 0 | 0
Retail Stores, Sales Floors and Showroom Floors:
Dressing Rooms: | 0.25 | 0 |  | 0
Specialty Shops:
Auto Motor fuel-dispensing station: | 1.5 | 0 |  | 0
Barber: | 0.5 | 0 |  | 0
Beauty Salon: | 0.6 | 0 |  | 0
Embalming Room: | 2 | 0 |  | 0
Nail Salon: | 0.6 | 0 |  | 0
Pet Shops (Animal area): | 0.9 | 0 |  | 0
Sports and Amusement:
Ice Arenas without Combustion Engines: | 0.5 | 0 |  | 0
Storage:
Repair garages, Enclosed parking garages: | 0.75 | 0 |  | 0
Workrooms:
Copy, Printing rooms | 0.5 | 0 |  | 0
Darkrooms: | 1 | 0 |  | 0
Total Exhaust Required: | 0 | CFM

## 2024 IMC Exhaust Rqmts
IMC Table 403.3.1.1
Occupancy Classification: | Exhaust Rate: | Square Footage: | # of Fixtures: | Exhaust CFM Required:
Animal Facilities
Animal Imaging (MR/CT/PET): | 0.9 | 0 |  | 0
Animal Operating Room: | 3 | 0 |  | 0
Animal PostOp Recovery Room: | 1.5 | 0 |  | 0
Animal Preperation Room: | 1.5 | 0 |  | 0
Animal Procedure Room: | 2.25 | 0 |  | 0
Animal Surgery Scrub: | 1.5 | 0 |  | 0
Large-Animal Holding Room: | 2.25 | 0 |  | 0
Necropsy: | 2.25 | 0 |  | 0
Small-Animal Cage Room (Static Cages): | 2.25 | 0 |  | 0
Small-Animal Cage Room (Ventilated Cages): | 1.5 | 0 |  | 0
Correction Facilities:
Cells W/ Plumbing Fixtures: | 1 | 0 |  | 0
Education:
Art Classroom: | 0.7 | 0 |  | 0
Locker/Dressing Rooms: | 0.25 | 0 |  | 0
Science Laboratories: | 1 | 0 |  | 0
Sports Locker Rooms: | 0.5 | 0 |  | 0
Wood / Metal Shops: | 0.5 | 0 |  | 0
Food and Beverage:
Kitchens (cooking): | 0.7 | 0 |  | 0
Hotels, Motels, Resorts, and Dormatories:
Bathrooms/Toilet - Private (Cont. Running Fan): | 25 |  | 0 | 0
Bathrooms/Toilet - Private (Intermediate Fan): | 50 |  | 0 | 0
Private Dwellings, Single and Multiple:
Garages, common for multi units: | 0.75 | 0 |  | 0
Kitchens (Cont. Running Fan): | 50 |  | 0 | 0
Kitchens (Intermediate Fan): | 100 |  | 0 | 0
Toilet Rooms and Bathrooms (Cont. Running Fan): | 25 |  | 0 | 0
Toilet Rooms and Bathrooms (Intermediate Fan): | 50 |  | 0 | 0
Public Spaces:
Elevator Car: | 1 | 0
Room with adult changing station (Cont. Running Fan): | 50 |  | 0 | 0
Room with adult changing station (Intermediate Fan): | 70 |  | 0 | 0
Shower room (per shower head) (Cont. Running Fan): | 20 |  | 0 | 0
Shower room (per shower head) (Intermediate Fan): | 50 |  | 0 | 0
Toilet Rooms - Public (Cont. Running Fan): | 50 |  | 0 | 0
Toilet Rooms - Public (Intermediate Fan): | 70 |  | 0 | 0
Retail Stores, Sales Floors and Showroom Floors:
Dressing Rooms: | 0.25 | 0 |  | 0
Specialty Shops:
Auto Motor fuel-dispensing station: | 1.5 | 0 |  | 0
Barber: | 0.5 | 0 |  | 0
Beauty Salon: | 0.6 | 0 |  | 0
Embalming Room: | 2 | 0 |  | 0
Nail Salon: | 0.6 | 0 |  | 0
Pet Shops (Animal area): | 0.9 | 0 |  | 0
Sports and Amusement:
Ice Arenas without Combustion Engines: | 0.5 | 0 |  | 0
Storage:
Repair garages, Enclosed parking garages: | 0.75 | 0 |  | 0
Workrooms:
Copy, Printing rooms | 0.5 | 0 |  | 0
Darkrooms: | 1 | 0 |  | 0
Total Exhaust Required: | 0 | CFM

## 2009 - 2021 UMC Exhaust Rqmts
UMC Table 403.7
Occupancy Classification: | Exhaust Rate: | Square Footage: | # of Fixtures: | Exhaust CFM Required:
Arenas: | 0.5 | 0 |  | 0
Art Classrooms: | 0.7 | 0 |  | 0
Auto Repair Rooms: | 1.5 | 0 |  | 0
Barber Shops: | 0.5 | 0 |  | 0
Beauty and Nail Salons: | 0.6 | 0 |  | 0
Cell with toilet: | 1 | 0 |  | 0
Copy, Printing rooms: | 0.5 | 0 |  | 0
Darkrooms: | 1 | 0 |  | 0
Educational Science Laboratories: | 1 | 0 |  | 0
Janitor closet, Trash rooms, recylcing: | 1 | 0 |  | 0
Kitchens - Commercial: | 0.7 | 0 |  | 0
Kitchenettes: | 0.3 | 0 |  | 0
Locker rooms for athletic, industrial, and Health care facilities: | 0.5 | 0 |  | 0
Other Locker rooms: | 0.25 | 0 |  | 0
Parking Garages: | 0.75 | 0 |  | 0
Pet Shops (animal areas): | 0.9 | 0 |  | 0
Soiled Laundry Storage: | 1 | 0 |  | 0
Storage rooms, Chemical: | 1.5 | 0 |  | 0
Woodowork shop/classrooms: | 0.5 | 0 |  | 0
Bathroom - Private (Cont. running fan): | 25 |  | 0 | 0
Bathroom - Private (Intermediate fan): | 50 |  | 0 | 0
Shower rooms - per head (Cont. running fan): | 20 |  | 0 | 0
Shower rooms - per head (Intermediate fan): | 50 |  | 0 | 0
Residential Kitchens (Cont. running fan): | 50 |  | 0 | 0
Residential Kitchens (Intermediate fan): | 100 |  | 0 | 0
Toilets - Public (Cont. running fan): | 50 |  | 0 | 0
Toilets - Public: | 70 |  | 0 | 0
Total Exhaust Required: | 0 | CFM

## 2024 UMC Exhaust Rqmts
UMC Table 403.7
Occupancy Classification: | Exhaust Rate: | Square Footage: | # of Fixtures: | Exhaust CFM Required:
Animal Imaging (MRI/CT/PET): | 0.9 | 0 |  | 0
Animal Operating Rooms: | 3 | 0 |  | 0
Animal PostOp Recovery Room: | 1.5 | 0 |  | 0
Animal Preperation Rooms: | 1.5 | 0 |  | 0
Animal Procedure Room: | 2.25 | 0 |  | 0
Animal Surgery Scrub: | 1.5 | 0 |  | 0
Large Animal Holding Room: | 2.25 | 0 |  | 0
Necropsy: | 2.25 | 0 |  | 0
Small-Animal Cage Room (Static Cages): | 2.25 | 0 |  | 0
Snall-Animal Cage Room (Ventilated Cages): | 1.5 | 0 |  | 0
Arenas: | 0.5 | 0 |  | 0
Art Classrooms: | 0.7 | 0 |  | 0
Auto Repair Rooms: | 1.5 | 0 |  | 0
Barber Shops: | 0.5 | 0 |  | 0
Beauty and Nail Salons: | 0.6 | 0 |  | 0
Cell with toilet: | 1 | 0 |  | 0
Copy, Printing rooms: | 0.5 | 0 |  | 0
Darkrooms: | 1 | 0 |  | 0
Educational Science Laboratories: | 1 | 0 |  | 0
Janitor closet, Trash rooms, recylcing: | 1 | 0 |  | 0
Kitchens - Commercial: | 0.7 | 0 |  | 0
Kitchenettes: | 0.3 | 0 |  | 0
Locker rooms for athletic, industrial, and Health care facilities: | 0.5 | 0 |  | 0
Other Locker rooms: | 0.25 | 0 |  | 0
Parking Garages: | 0.75 | 0 |  | 0
Pet Shops (animal areas): | 0.9 | 0 |  | 0
Soiled Laundry Storage: | 1 | 0 |  | 0
Storage rooms, Chemical: | 1.5 | 0 |  | 0
Woodowork shop/classrooms: | 0.5 | 0 |  | 0
Bathroom - Private (Cont. Running Fan): | 25 |  | 0 | 0
Bathroom - Private (Intermediate Fan): | 50 |  | 0 | 0
Shower rooms (Per Head) (Cont. Running Fan): | 20 |  | 0 | 0
Shower rooms (Per Head) (Intermediate Fan): | 50 |  | 0 | 0
Residential Kitchens (Cont. Running Fan): | 50 |  | 0 | 0
Residential Kitchens (Intermediate Fan): | 100 |  | 0 | 0
Toilets - Public (Cont. Running Fan): | 50 |  | 0 | 0
Toilets - Public (Intermediate Fan): | 70 |  | 0 | 0
Total Exhaust Required: | 0 | CFM