## Sheet1
2025 California Energy Code:
Commercial (Section 130.1):
1. (2) Means of control are required for all lighting.
A. Dimming / Occupancy sensor
|  | Exceptions: | 1. Restroom (no size limitation) / single control.
2. Rooms 100 sq. ft. of less and lighting load less than 0.5 watts per sq. ft.
3. Enclosed areas with (1) light and has no more than (2) lamps.
4. Healthcare facilities.
| Note: | Commercial R.R. lights and exhaust fans can be controlled by single occupancy sensor.
B. In office spaces greater than 250 s. ft., occupancy sensors shall be configured so that lighting
shall be controlled in control zones no greater than 600 sq. ft. each.
Residential (Section 150.0(k)):
1. Occupancy sensors are required at:
A. Bathrooms
B. Laundry room(s)
C. Utility room(s)
2. Any wired boxes for future lights or fans above 5'-0" a.f.f. must be controlled by one of the following:
A. Occpucany / vacancy sensors
B. Dimming Switch
C. Fan Speed Control
3. Recessed lighting to be controlled by:
A. Dimmming Switches
4. LED lighting to be controlled by:
A. Dimmming Switches
|  | Exceptions: | 1. Lights in closets less than 70 s.f. (std. toggle switch)
2. Lights in hallways (std. toggle switch)
5. Pin-Based Flourescents with electronic ballast:
A. Std. toggle switch
6. Exhaust fans are required to be switched separate from light.
A. Std. toggle switch
Daylight control (Section 130.1(d)):
Momentary / Occupancy / Photosensor is required.
| Exceptions: | 1. In enclosed rooms / spaces where the daylight zone combined lighting is
75 watts or less.
2. Retail merchandise zones and wholesale show room areas.
3. Rooms that have a total glazing of less than 24 sq. ft.
| Note: | 1. Daylight zone length is header height (example: header @ 81", length is 81")
2. Daylight zone width is header height divded by 2 (example: 81" / 2 = 40.5")
3. Skylit Daylit Zone radius is ceiling height X 0.7. from outer edge of skylight.
(example: ceiling @ 8'-0"" X 0.7 = 5'-6" from outter edges)
Link: | https://codes.iccsafe.org/content/CAEC2025P1/subchapter-4-nonresidential-and-hotel-motel-occupancies-mandatory-requirements-for-lighting-systems-and-equipment-and-electrical-power-distribution-systems
2022 California Energy Code:
Commercial (Section 130.1):
1. (2) Means of control are required for all lighting.
A. Dimming / Occupancy sensor
|  | Exceptions: | 1. Restroom (no size limitation) / single control.
2. Rooms 100 sq. ft. of less and lighting less than 0.5 watts per sq. ft.
3. Enclosed areas with (1) light and has no more than (2) lamps.
4. Healthcare facilities.
| Note: | Commercial R.R. lights and exhaust fans can be controlled by single occupancy sensor.
Residential (Section 150.0(k)):
1. Occupancy sensors are required at:
A. Bathrooms
B. Laundry room(s)
C. Utility room(s)
2. Any wired boxes for future lights or fans above 5'-0" a.f.f. must be controlled by one of the following:
A. Occpucany / vacancy sensors
B. Dimming Switch
C. Fan Speed Control
3. Recessed lighting to be controlled by:
A. Dimmming Switches
4. LED lighting to be controlled by:
A. Dimmming Switches
|  | Exceptions: | 1. Lights in closets less than 70 s.f. (std. toggle switch)
2. Lights in hallways (std. toggle switch)
5. Pin-Based Flourescents with electronic ballast:
A. Std. toggle switch
6. Exhaust fans are required to be switched separate from light.
A. Std. toggle switch
Daylight control (Section 130.1(d)):
Momentary / Occupancy switch is required.
| Exceptions: | 1. In rooms / spaces where the daylight zone combined lighting is less than
120 watts.
2. Retail merchandise zones and wholesale show room areas.
3. Rooms that have a total glazing of less than 24 sq. ft.
| Note: | 1. Daylight zone length is header height (example: header @ 81", length is 81")
2. Daylight zone width is header height divded by 2 (example: 81" / 2 = 40.5")
3. Skylit Daylit Zone radius is ceiling height X 0.7. from outer edge of skylight.
(example: ceiling @ 8'-0"" X 0.7 = 5'-6" from outter edges)
Link: | https://codes.iccsafe.org/content/CAEC2022P3/subchapter-4-nonresidential-and-hotel-motel-occupancies-mandatory-requirements-for-lighting-systems-and-equipment-and-electrical-power-distribution-systems#CAEC2022P3_Ch04_Sec130.0
2024 IECC Lighting controls:
Commercial (Section C405.2.1):
1. Occupancy sensors are required @:
A. Classrooms / Lecture / Training rooms (Dimming controls also required, C405.2.3)
B. Computer room, data center
C. Conference / Meeting / Multi-purpose rooms (Dimming controls also required, C405.2.3)
D. Copy / Print rooms
E. Lounges / breakrooms (Dimming controls also required, C405.2.3)
F. Medicall supply room in a health care facitility
G.Enclosed offices (Dimming controls also required, C405.2.3)
H. Restrooms
I. Storage rooms
J. Telemedicine room in a health care facility (See C405.2.3)
K. Locker rooms
L. Corridors
|  | C405.2.1.4: | Occupancy sensor controls in corridor shall uniformly reduce lighting power to not more than 50 percent of full power.
M. other spaces 300 square feet or less that are enclosed by floor-to-ceiling height partitions
N. Warehouse Storage Areas
|  | C405.2.1.2: | 1. Lighting in each aisleway shall be controlled independently of lighting in all other aisleways and open areas.
2. Occupant sensors shall be automatically reduce lighting power within each controlled area to an occupied setpoint of not more than 50%.
3. Lights that are not turned off by occupant sensors shall be turned off by time-switch control complying w/ C405.2.2.1.
4. A manual control shall be provided to allow occupants to turn off lights in the space.
O. Open Office Spaces: Occ sensors shall be configured to the general lighitng floor area
does not exceed 600 sq. ft. (C405.2.1.3, Note 1)
2. In spaces / areas not provided with an occupancy sensor shall be provided with a timed-switch control. (C405.2.2)
3. Dimming Controls required at the following spaces (in addition to occupancy sensors, as applicable) (NEW C405.2.3):
A. Classrooms / Lecture / Training rooms
B. Conference / mulipurpose / meeting rooms.
C. Dining area for bar / lounge or leisure, family dancing.
D. Laboratory.
E. Lobby.
F. Loung / breakroom
G. Offices
H. Gymnasiums / fitness center.
I. Library reading room
J. Health care facility for imaging rooms, exam rooms, nursery, and nurses' station.
K.Spaces not provided with occupancy sensors.
Note: Reduced lighting controls have been removed from the 2024 IECC.
2024 IECC Lighting controls Continued:
Sleeping Units and Dwelling Units in hotels, motels and vacation timeshare prop. (Section C405.2.10.1):
1. Min. (1) 15- and 20-amp switched receptacle in each roof, except for bathrooms, kitchens, foyers, hallways and closets.
2. Lighting controls that automatically turn off all lighting and switched receptacles within 20 minutes after all occupants have left the unit
Sleeping Units in Congregate Living Facilities (Section C405.2.10.1):
1. Lighting in bathrooms shall be controlled by an occupant sensor.
2. Each unit shall have a manual control by the entrance that turns off all lighting and switched receptacles in the unit, except for lighting in bathrooms and kitchens. The manual control shall be marked to indicate its function.
Residential (Section R404.2):
1. Habitable spaces: Manual dimmer OR automatic shutoff (Occ. Sensor) is required. (R404.2.1)
2. Exterior controls for Individual dwelling units with exterior lighting exceeding 30 watts. (R404.3, R404.3.1)
A. Shall be controlled by a switch.
B. Shall have photo sensor.
C. Shall have a timer.
Daylight control (Section C405.2.4):
Momentary or Toggle / Occupancy switch is required.
| Exceptions: | 1. In rooms / spaces where the primary daylight zone combined lighting is less than 75 watts. (Note 1)
2. In rooms / spaces where the daylight zone combined lighting is less than 150 watts. (Note 2)
3. In rooms / spaces where the toplit daylight zone combined lighting is less than 75 watts. (Note 3)
4. Spaces in health care facilities where patient care is directly provided. (Exception 1)
5. Sidelight daylight zones on the first floor above grade in Groups A-2 & M occupancies. (Exception 2)
6. Enclosed office spaces less than 250 sq. ft.. (Exception 3)
Daylight Zone(s) (Section C405.2.4.2):
1. Primary Daylight zone length is header height (example: header @ 81", length is 81" from window)
2. Secondary Daylight zone length is header height X 2 (example: header @ 81", length is 162" from window)
2. Daylight zone width is 2'-0" each side of window each side of winow / sidelite
3. Skylit Daylit Zone radius is ceiling height X 0.7. from outer edge of skylight.
(example: ceiling @ 8'-0"" X 0.7 = 5'-6" from outter edges)
Link: | https://codes.iccsafe.org/content/IECC2024P1/chapter-4-ce-commercial-energy-efficiency#IECC2024P1_CE_Ch04_SecC405
2021 IECC Lighting controls:
Commercial (Section C405.2.1):
1. Occupancy sensors are required @:
A. Classrooms / Lecture / Training rooms
B. Conference / Meeting / Multi-purpose rooms
C. Copy / Print rooms
D. Lounges / breakrooms
E. Break rooms
F. Private offices
G. Restrooms
H. Storage rooms
I. Locker rooms
J. Corridors (New)
|  | C405.2.1.4: | Occupancy sensor controls in corridor shall uniformly reduce lighting power to not more than 50 percent of full power.
K. other spaces 300 square feet or less that are enclosed by floor-to-ceiling height partitions
L. Warehouse Storage Areas
|  | C405.2.1.2: | 1. Lighting in each aisleway shall be controlled independently of lighting in all other aisleways and open areas.
2. Occupant sensors shall be automatically reduce lighting power within each controlled area to an occupied setpoint of not more than 50%.
3. Lights that are not turned off by occupant sensors shall be turned off by time-switch control complying w/ C405.2.2.1.
4. A manual control shall be provided to allow occupants to turn off lights in the space.
M. Open Office Spaces: Occ sensors shall be configured to the general lighitng floor area does not exceed 600 sq. ft. (C405.2.1.3)
2. Spaces not listed above require Light-reduction controls (C405.2.3)
A. Dual lighting controls (toggle switches)
B. Dimming switch
|  | Exception: | 1. Light reduction controls are not required in daylight zones
2. Luminaires controlled by special application controls (See C405.2.5)
3. Where provided with manual controls, the following areas are not required to have light reduction controls.
3.1. spaces that have only (1) light with less than 60W.
3.2. Spaces that use less than 0.45W per square foot.
3.3. Corridors, lobbies, electrical rooms, and/or mechanical rooms.
Residential (Section R404.2):
1. Dimmer, occupancy sensor, or control that is installed or built into the fixture
| Exceptions: | 1. Bathrooms
2. Hallways
3. Exterior lighting fixtures
4. Lights designed for safety or security
2021 IECC Lighting controls Continued:
Daylight control (Section C405.2.3):
Momentary or Toggle / Occupancy switch is required.
| Exceptions: | 1. In rooms / spaces where the daylight zone combined lighting is less than 150 watts.
2. Lighting that is required to have specific application control in accordance with Section C405.2.4.
3. Sidelight daylight zones on the first floor above grade in Groups A-2 & M occupancies.
4. Spaces in health care facilities where patient care is directly provided.
5. New buildings where the total connected lighting power calculated is accordance with Section C405.3.1 is not greater than the interior lighting power allowance calculated in accordance with equation 4-9.
Daylight Zone(s) (Section C405.2.4.2):
1. Primary Daylight zone length is header height (example: header @ 81", length is 81" from window)
2. Secondary Daylight zone length is header height X 2 (example: header @ 81", length is 162" from window)
2. Daylight zone width is 2'-0" each side of window each side of winow / sidelite
3. Skylit Daylit Zone radius is ceiling height X 0.7. from outer edge of skylight.
(example: ceiling @ 8'-0"" X 0.7 = 5'-6" from outter edges)
Link: | https://codes.iccsafe.org/content/IECC2021P2/chapter-4-ce-commercial-energy-efficiency#IECC2021P2_CE_Ch04_SecC405
2018 IECC Lighting controls:
Commercial (Section C405.2):
1. Occupancy sensors are required @:
A. Classrooms / Lecture / Training rooms
B. Conference / Meeting / Multi-purpose rooms
C. Copy / Print rooms
D. Lounges
E. Break rooms
F. Private offices
G. Restrooms
H. Storage rooms
I. Janitorial closets
J. Locker rooms
K. other spaces 300 square feet or less that are enclosed by floor-to-ceiling height partitions
L. Warehouses (Note special control requirements per Section C405.2.1.2)
|  | Exceptions: | 1. Areas designated as security or emergency areas that are required
to be continuously lighted.
2. Interior exit stairways, interior exit ramps and exit passageways.
3. Emergency egress lighting that is normally off.
M. Open Office Spaces: Occ sensors shall be configured to the general lighitng floor area does not exceed 600 sq. ft. (C405.2.1.3)
2. Spaces not listed above require either:
A. Dual lighting controls (toggle switches)
B. Dimming switch
|  | Exception: | 1. Light reduction controls are not required in daylight zones
Residential (Section R404):
1. Single toggle switch in all spaces.
Daylight control (Section C405.2.3):
Momentary / Occupancy switch is required.
| Exceptions: | 1. In rooms / spaces where the daylight zone combined lighting is less than
150 watts.
2. Lighting that is required to have specific application control in accordance
with Section C405.2.4.
3. Sidelight daylight zones on the first floor above grade in Groups A-2 & M
ccupancies.
4. Spaces in health care facilities where patient care is directly provided.
5. New buildings where the total connected lighting power calculated is
accordance with Section C405.3.1 is not greater than the interior lighting power
allowance calculated in accordance with equation 4-9.
| Note: | 1. Daylight zone length is header height (example: header @ 81", length is 81")
2. Daylight zone width is 2'-0" each side of window each side of winow / sidelite
3. Skylit Daylit Zone radius is ceiling height X 0.7. from outer edge of skylight.
(example: ceiling @ 8'-0"" X 0.7 = 5'-6" from outter edges)
Link: | https://codes.iccsafe.org/content/IECC2018P5/chapter-4-ce-commercial-energy-efficiency#IECC2018P5_CE_Ch04_SecC405
2015 IECC Lighting controls:
Commercial (Section C405.2):
1. Occupancy sensors are required @:
A. Classrooms / Lecture / Training rooms
B. Conference / Meeting / Multi-purpose rooms
C. Copy / Print rooms
D. Lounges
E. Employee lunch / Break rooms
F. Private offices
G. Restrooms
H. Storage rooms
I. Janitorial closets
J. Locker rooms
K. other spaces 300 square feet or less that are enclosed by floor-to-ceiling height partitions
L. Warehouses (Note special control requirements per Section C405.2.1.2)
|  | Exceptions: | 1. Areas designated as security or emergency areas that are required
to be continuously lighted.
2. Interior exit stairways, interior exit ramps and exit passageways.
3. Emergency egress lighting that is normally off.
2. Spaces not listed above require either:
A. Dual lighting controls (toggle switches)
B. Dimming switch
|  | Exception: | 1. Light reduction controls are not required in daylight zones
Residential (Section R404):
1. Single toggle switch in all spaces.
Daylight control (Section C405.2.3):
Momentary / Occupancy switch is required.
| Exceptions: | 1. In rooms / spaces where the daylight zone combined lighting is less than
150 watts.
2. Dwelling / Sleeping units.
3. Sidelight daylight zones on the first floor above grade in Groups A-2 & M
ccupancies.
4. Spaces in health care facilities where patient care is directly provided.
| Note: | 1. Daylight zone length is header height (example: header @ 81", length is 81")
2. Daylight zone width is 2'-0" each side of window each side of winow / sidelite
3. Skylit Daylit Zone radius is ceiling height X 0.7. from outer edge of skylight.
(example: ceiling @ 8'-0"" X 0.7 = 5'-6" from outter edges)
Link: | https://codes.iccsafe.org/content/IECC2015/chapter-4-ce-commercial-energy-efficiency#IECC2015_Pt01_Ch04_SecC405
2012 IECC Lighting controls:
Commercial (Section C405.1):
1. Occupancy sensors are required @:
A. Classrooms
B. Conference / Meeting rooms
C. Employee lunch / Break rooms
D. Private offices
E. Restrooms
F. Storage rooms
G. Janitorial closets
H. other spaces 300 square feet or less that are enclosed by floor-to-ceiling height partitions
2. Spaces not listed above require either:
A. Dual lighting controls (toggle switches)
|  | Exceptions: | 1. Areas that have (1) luminaire with rated power less than 100 watts.
2. Areas controlled by occupancy sensors
3. Corridors, equip. rooms, storerooms, restrooms, public lobbies,
electrical or mechanicalrooms.
4. Sleeping unit.
5. Spaces that use less than 0.6 watts per square foot.
6. Daylight spaces complying with Section C405.2.2.3.2
Residential (Section R404):
1. Single toggle switch in all spaces.
Daylight control (Section C405.2.2.3):
Momentary / Occupancy switch is required.
| Exception: | 1. Zones enclosed by walls or ceiling height partitions and containing (2) or fewer
light fixtures are not required to have a separate switch for general are lighting.
Note: | 1. Daylight zone length is 15'-0"
2. Daylight zone width is 2'-0" each side of window each side of winow / sidelite
3. Skylit Daylit Zone radius is ceiling height from outer edges of skylight.
(example: ceiling @ 8'-0" = 8'-0" from outter edges)
Link: | https://codes.iccsafe.org/content/IECC2012P5/chapter-4-ce-commercial-energy-efficiency#IECC2012_Pt01_Ch04_SecC405
2009 IECC Lighting controls:
Commercial (Section 505.1):
1. Occupancy sensors are required @:
A. Buildings larger than 5,000 sq. ft.
|  | Exceptions: | 1. Sleeping unit
2. Lighting in spaces where patient care is directly provided.
3. Spaces where an automatic shutoff would endager occupant safety
or security.
2. If less than 5,000 sq. ft.:
A. Dual lighting controls (toggle switches)
|  | Exceptions: | 1. Areas that have (1) luminaire.
2. Areas controlled by occupancy sensors
3. Corridors, storerooms, restrooms, public lobbies,
4. Sleeping unit.
5. Spaces that use less than 0.6 watts per square foot.
Residential (Section 404):
1. Single toggle switch in all spaces.
Daylight control (Section 505.2.2.3):
Momentary / Occupancy switch is required.
| Exception: | 1. Zones enclosed by walls or ceiling height partitions and containing (2) or fewer
light fixtures are not required to have a separate switch for general are lighting.
Note: | 1. Daylight zone length is 15'-0"
2. Daylight zone width is 2'-0" each side of window each side of winow / sidelite
3. Skylit Daylit Zone radius is ceiling height from outer edges of skylight.
(example: ceiling @ 8'-0" = 8'-0" from outter edges)
Link: | https://codes.iccsafe.org/content/IECC2009P10/chapter-5-commercial-energy-efficiency#IECC2009P10_Ch05_Sec505