## Voltage Calc
VOLTAGE DROP CALCULATIONS:
Vd = Voltage Drop | [9 empty] | Coductor Type (@ 75 degrees C):
I = Current in Conductor (Amperes) | [9 empty] | Copper
L = One-way Length of Circuit (Feet) | [12 empty] | Notes:
Cm = Cross Section Area of Conductor (Circular Mills) | [10 empty] | 120 | Calc 1 | Circuit Amerpage (I) Examples:
K = Resistance in Ohms of 1 circular Mill Foot of Conductor | [10 empty] | 120 | Calc 2 | 4 standard receptacles at 180 watts (120v) =
| K = | 12.9 | [8 empty] | 120 | Calc 3 | 4 X 180 = 720 Watts
[11 empty] | 120 | Calc 4 | 720 Watts / 120(v) = 6 Amps
Formula (For Single Phase) | [6 empty] | Formula (For Three Phase)
|  | Vd = | 2K x L x I |  |  |  |  | Vd = | 1.73K x L x I |  |  |  | 1 Dedicated Receptacle at 3,840 watts (240v)=
|  |  | Cm | [5 empty] | Cm |  |  |  | 1 X 3,840 = 3,840 Watts
Calc 1: | [9 empty] | Circuit #: |  |  | 3,840 Watts / 240(v) = 16 Amps
| Circuit Phase: |  |  | Wire Size: |  |  | Length of Wire (L): |  |  | Amps of Circuit (I): |  |  | Note: You do not need to take the breaker size for the Amperage, but rather the connected load to that breaker.
| 120V 1P |  |  | 12
2 | X | 12.9 | X | 0 | X | 0 | = | 0 | Volts |  |  |  | Wire Length (L):
6530 | [12 empty] | Consider the wire length up / down the wall(s) to the furtherest lighth, receptacle, equipment, etc.
Percentage Drop: | [12 empty] | Note: Be slightly conservative with the total developed wire length.
0 | / | 120 | = | 0 | %, (Vd) less than 3% drop therefore OK
Calc 2: | [9 empty] | Circuit #: |  |  | Requirements:
| Circuit Phase: |  |  | Wire Size: |  |  | Length of Wire (L): |  |  | Amps of Circuit (I): |  |  | See NEC, Article 210.19 for requirement(s)
| 120V 1P |  |  | 12 | [8 empty] | See IECC, Section C405.11
See Ashrea 90.1, Section 8.4.1
2 | X | 12.9 | X | 0 | X | 0 | = | 0 | Volts
6530
Percentage Drop:
0 | / | 120 | = | 0 | %, (Vd) less than 3% drop therefore OK
Calc 3: | [9 empty] | Circuit #:
| Circuit Phase: |  |  | Wire Size: |  |  | Length of Wire (L): |  |  | Amps of Circuit (I):
| 120V 1P |  |  | 12
2 | X | 12.9 | X | 0 | X | 0 | = | 0 | Volts
6530
Percentage Drop:
0 | / | 120 | = | 0 | %, (Vd) less than 3% drop therefore OK
Calc 4: | [9 empty] | Circuit #:
| Circuit Phase: |  |  | Wire Size: |  |  | Length of Wire (L): |  |  | Amps of Circuit (I):
| 120V 1P |  |  | 12
2 | X | 12.9 | X | 0 | X | 0 | = | 0 | Volts
6530
Percentage Drop:
0 | / | 120 | = | 0 | %, (Vd) less than 3% drop therefore OK

## Circular Mills
Wire Size | Cir. Mils
18 | 1620
16 | 2580
14 | 4110
12 | 6530
10 | 10380
8 | 16510
6 | 26240
4 | 41740
3 | 52620
2 | 66360
1 | 83690
1/0 | 105600
2/0 | 133100
3/0 | 167800
4/0 | 211600
250 kcmil | 250000
300 kcmil | 300000
350 kcmil | 350000
400 kcmil | 400000
500 kcmil | 500000
600 kcmil | 600000
700 kcmil | 700000
750 kcmil | 750000
800 kcmil | 800000
900 kcmil | 900000
1000 kcmil | 100000
1250 kcmil | 125000
1500 kcmil | 150000
1750 kcmil | 175000
2000 kcmil | 200000