For Sales

- 103.6

  - Need to provide as built drawings that include electric and solar ready design to customers as well as compliance documentation and supporting calculations to customer for every building.

- 104.2.1

  - Discuss how much extra panel space and capacity we need for solar equipment circuit breakers.  May need to upsize panels or amend elect calculator.

- CE301.1.1

  - On site inspection may be necessary before Certificate of Occupancy is released depending on scope of electric ready done in factory.

- CE302.2.1

  - Extra panel space and capacity for electric Bards or splits when putting combustion Bards/Splits in.

  - Need to let dealer know MDP will need upsized.

- CS402.3

  - Need 40% roof coverage for solar-ready zone.

    - Do we need to increase number of joists to 16” O/C for 40% of roof?

- CS402.7

  - Main electrical panel amperage of at least 200 amps.

- CV502

  - Do we exclude the electric vehicle package for the main distribution panel?  Need to update dealer during quote.

- CV502.1.6

| Building Type | EVSE Installed Space | EV Ready Space | EV Capable Light Space | EV Capable Light Space |
| --- | --- | --- | --- | --- |
| B with Occ <= 10 | 0 | 2 Spaces | 0 | 0 |
| B with Occ > 10 | 2% of Spaces | 8% of Spaces | 10% of Spaces | 10% of Spaces |
| R2 with Occ <= 10 | 0 | 15% of Spaces | 10% of Spaces | 10% of Spaces |
| R2 with Occ >10 | 5% of Spaces | 15% of Spaces | 10% of Spaces | 30% of Spaces |

For Design

- CS402.6

  - Show conduit pathway for solar-ready zone as “Potential Pathway”.

- CS402.7 & CS410.2

  - Title space for solar in the panel schedule as “For Future Solar Electric”.

  - Reserved space shall be positioned at the opposite (load) end from the input feeder location or main circuit location.