UTAH CODE AMANDEMENTS:

- Applicable Codes:

  - 2021 IBC

  - 2021 IRC

  - 2021 IPC

  - 2021 IMC

  - 2020 NEC

  - 2021 IECC

  - ICC A117.1-2009 Accessibility

  - ICC/MBI 1200 & 1205 – 2021

- (IBC – 305.2) For Group E child daycare facilities classified as a Group E, the age changed from 2-1/2 year to 2 years or greater.

- (IBC – 907.2.3.1 – Added – Applies to Group E Occupancies) Automatic smoke detection devices shall be installed throughout all corridors and spaces open to the corridor at a max spacing of 30 feet on center and no more than 15 feet from walls or smoke detectors.

- (IBC – 907.2.3.2 – Added – Applies to Group E Occupancies) When a sprinkler system is not installed, automatic smoke detectors are required.

- (ICC/MBI 1205, Chapter 7) Ground snow loads will be required on drawings and data plates.  See attached for ground snow loads by city / county.

- (IBC Chapter 35) Referenced standard for Accessibility was changed to A117.1-2009.

- (IPC Table 403.1 – NEW / ADDED) When providing public toilet facilities, there shall be an equal number of diaper changing facilities in male / female toilet rooms.

- (IPC Section 405.3.5) When multi-use toilet facilities are provided for all genders, the partitions must extend from floor-to-ceiling.

- (IPC Section 413.5 – NEW / ADDED) Floor drains are required in all public restrooms (single user or multi-user).

- (NEC 210.8) Removed GFCI requirements on 230/240V receptacles

- (NEC 210.65) Removed electrical requirements for Meeting Rooms (floor receptacles not required and spacing at 6’/12’ not required).

- (IECC C405.11) Controlled receptacles are not required and shall be optional and decided by the property owner.

The following Local amendments are adopted:

- Park City Corp or Park City Fire District:

  - New construction of more than 6,000 square feet requires a sprinkler system.

  - New construction 3 stories or greater requires a sprinkler system.

- Sandy City:

  - Appendix N, Added WUI (Wildland Urban Interface).  Customer will need to verify with local officials if WUI will apply based on site location.