C406.2.2.6 High Performance Dedicated Outdoor Air System (DOAS)

No less than 90 percent of the total conditioned floor area of the whole project, excluding floor area of unoccupied spaces that do not require ventilation as specified by the International Mechanical Code, shall be served by DOAS installed in accordance with Section C403.3.5 with the following adjustments:

- Minimum heat recovery sensible effectiveness of 80 percent, calculated in accordance with Section C403.3.5.1.

- Where design outdoor airflow is greater than 500 cfm (250 L/s), the DOAS shall be equipped with an economizer bypass, damper control, or wheel speed control that is active between 55°F (13°C) and 75°F (24°C) outdoor air temperature and minimizes energy recovery or maintains an appropriate DOAS leaving air temperature when the building is generally in cooling, based either on outdoor air temperature or a DDC zone-based cooling system reset.

- DOAS total combined fan power shall be less than either:

  - 0.769 W/cfm (1.55 W/L/s) when calculated in accordance with Section C403.3.5.2.

  - Eighty percent of fan power allowance for a constant volume system when calculated in accordance with Section C403.8.1.

C403.3.5.1 DOAS With Energy Recovery Ventilation

The DOAS shall include energy recovery. The energy recovery device shall have a 68 percent minimum sensible recovery effectiveness as calculated in accordance with Equation 4-9 or provide an enthalpy recovery ratio of not less than 60 percent at design conditions in accordance with Section C403.7.6. The airflow rate thresholds in Section C403.7.6 that define when the energy recovery requirements in that section do not apply, are not applicable to this section. The return/exhaust air stream temperature for heat recovery device selection shall be 70°F (21°C) at 30 percent relative humidity, or as calculated by the registered design professional.(Equation 4-9)Where:

| TOA | = | Design outdoor air dry bulb temperature entering the energy recovery device. |
| --- | --- | --- |
| TSA | = | Supply air dry bulb temperature leaving the energy recovery device at design temperatures and airflow conditions, as selected for the proposed DOAS unit(s). |
| TRA | = | Design return air dry bulb temperature. |

EXCEPTIONS:

- Systems installed for the sole purpose of providing makeup air for systems exhausting toxic, flammable, paint, or corrosive fumes or dust, dryer exhaust, or commercial kitchen hoods used for collecting and removing grease vapors and smoke.

- Heat recovery and energy recovery ventilators (H/ERV) that are rated and listed in accordance with HVI 920 can demonstrate compliance with the sensible recovery effectiveness requirement using the adjusted sensible recovery effectiveness (ASRE) rating of the equipment at 32°F test conditions. Applied flow rate for ASRE rating shall be no less than the design flow rate or the closest value interpolated between two listed flow rates.

- The energy recovery systems for Group R-2 occupancies are permitted to provide 60 percent minimum sensible heat recovery effectiveness in lieu of 68 percent sensible recovery effectiveness in accordance with Section C403.7.6. The return/exhaust air stream temperature for heat recovery device selection shall be 70°F (21°C) or as determined by an approved calculation procedure.